## SLM Data
|  |  | Filename | 24-004 ASTC-AIIC-NIC Test Report_1.2.1_
|  |  | Tab Name | SLM Data
| Project Name: | Ka'ulu by Gentry
| Project #: | P24-004 | [19 empty] | Max Def | Def SUM
| Client: | Gentry Builders, LLC | [17 empty] | ASTC
| Test Date: | 2024-04-04 | [17 empty] | 41 | Guess | 8 | 20
| Report Date: | 2024-04-18
| Source Room Name: | 2nd Floor Kitchen | [17 empty] | NIC
| Receiver Room Name: | 1st Floor Great Room/Kitchen | [17 empty] | 39 | Guess | 8 | 30
| Test Assembly Type: | Floor-ceiling | [23 empty] | Partition | Partition w. Window | Partition w. Door | Partition w. Window + Door | Floor/Ceiling | Floor
| Test #: | 1.2.1 | [17 empty] | AIIC
| Test Conducted By: | Zane Wright, Project Consultant | [17 empty] | 38 | Too high | 9 | 27
| and: | Jake Pfitsch, Project Consultant
ISR
| Test Environment Data | [18 empty] | 42 | Too high | 9 | 29
| Source Room Volume (ft3): | 3949 | 3950 |  | inches
| Receiver Room Volume (ft3): | 3949 | 3950 |  | 1 | 0.083333
| Test Partition Area (ft2): | 428 | 428 |  | 2 | 0.16667
| Test Partition Dimensions: | 14.8x29.583 |  |  | 5 | 0.41667
| The source room was | 2nd Floor Kitchen |  |  | 7 | 0.58333
| . The space was | finished unfurnished |  |  | 10 | 0.83333 | [19 empty] | unfinished and unfurnished | finished and unfurnished | finished and furnished
| . The floor was | LVT |  |  | 11 | 0.91667
| . The ceiling was | gyp
| . The walls were | gyp
All doors and windows were closed during the testing period.
Additional comments:
| The receiver room was | 1st Floor Great Room/Kitchen
| . The space was | finished unfurnished
| . The floor was | LVT
| . The ceiling was | gyp
| . The walls were | gyp
All doors and windows were closed during the testing period.
Additional comments:
| The tested assembly was the | Floor-ceiling
The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations.
| Does the test assembly perform as expected? | Yes | [23 empty] | Yes | No
| Reasons for reporting only NIC | [24 empty] | Yes | No
| Was Annex 2 used? | No
| Stock NIC notes: | The receiver and/or source room had a volume exceeding 150 m3 (5,300 cu. ft.), and the absorption of the receiver and/or source room was greater than the maximum allowed per E336-16, Paragraph 9.4.1.2.
The receiver and/or source room was not an enclosed space.
The receiver and/or source room has a volume less than the minimum volume requirement of 25 m3 (883 cu. ft.).
The receiver and/or source room has one or more dimensions less than the minimum requirement of 2.3 m (7.5 ft.).
| Reasons for reporting only ISR | The receiver room had a volume less than the minimum volume requirement of 40 m3. | [23 empty] | Yes | No
| Stock ISR notes: | The receiver and/or source room had a volume exceeding 150 m3 (5,300 cu. ft.), and the absorption of the receiver room was greater than the maximum allowed per E1007-16, Paragraph 10.3.1 and 10.4.5.
The receiver and/or source room was not an enclosed space.
The receiver and/or source room has a volume less than the minimum volume requirement of 40 m3 (1413 cu. ft.).
The receiver and/or source room has one or more dimensions less than the minimum requirement of 2.3 m (7.5 ft.).
Standards
| ASTC Test Procedure | ASTM E336-16 | Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings
| STC Calculation | ASTM E413-16 | Classification for Rating Sound Insulation
| AIIC Test Procedure | ASTM E1007-14 | Standard Test Method for Field Measurement of Tapping Machine Impact Sound Transmission Through Floor-Ceiling Assemblies and Associated Support Structure
| IIC Calculation | ASTM E989-06(2012) | Standard Classification for Determination of Impact Insulation Class (IIC)
| RT60 Test Procedure | ASTM E2235-04(2012) | Standard Test Method for Determination of Decay Rates for Use in Sound Insulation Test Methods
Test Equipment
|  | Model | Serial # | Last Calibration Date
| SLM D | 831 | 3784 | 2022-09-19
| Preamp | PRM831 | 051188 | 2022-09-19
| Mic | 377B20 | 301698 | 2022-09-16
| SLM E | 831 | 4328 | 2022-10-24
| Preamp | PRM831 | 046469 | 2022-10-24
| Mic | 377B20 | 168830 | 2022-10-20
| Calibrator (E) | CAL200 | 5955 | 2022-10-26
| Calibrator (D) | CAL200 | 2775671 | 2022-09-19
Frequency (Hz)
| ASTC / NIC Data | 831 File # | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000
| Pink Noise Source Room | E-556 | 95.8 | 95 | 91.4 | 90 | 91.6 | 89.7 | 88.8 | 84.7 | 82.5 | 84.5 | 83 | 83.8 | 81.4 | 79.8 | 82.4 | 84 | 85 | 84.3
| Pink Noise Receiver Room | D-529 | 78.2 | 79.5 | 73 | 65.6 | 61.6 | 57.6 | 52.7 | 47.5 | 42 | 40.4 | 35.1 | 32.4 | 30.2 | 27.5 | 24.1 | 21.6 | 19.7 | 18.1
| Receiver B.G. | E-542 | 35.4 | 39.2 | 33 | 37.1 | 34.4 | 33.7 | 33.3 | 32.5 | 31.2 | 30.6 | 29.6 | 28.9 | 28.5 | 24.9 | 20.6 | 18.5 | 17.6 | 15.1
| RT60 Average | E-RT057 | 0.61783 | 0.84579 | 0.63261 | 0.99566 | 1.0232 | 1.1372 | 1.3446 | 1.2621 | 1.1412 | 1.1179 | 1.2872 | 1.4592 | 1.5181 | 1.4609 | 1.3927 | 1.4027 | 1.3876 | 1.3159 | 617.8274 | 845.7884 | 632.6104 | 995.6555 | 1023.209 | 1137.202 | 1344.625 | 1262.11 | 1141.185 | 1117.875 | 1287.246 | 1459.191 | 1518.126 | 1460.914 | 1392.672 | 1402.743 | 1387.606 | 1315.864
|  |  | 617.8274 | 845.7884 | 632.6104 | 995.6555 | 1023.209 | 1137.202 | 1344.625 | 1262.11 | 1141.185 | 1117.875 | 1287.246 | 1459.191 | 1518.126 | 1460.914 | 1392.672 | 1402.743 | 1387.606 | 1315.864
AIIC Data
| Tapper Position #1 | E-543 | 78.6 | 79.7 | 74.9 | 72.9 | 76 | 72.5 | 68 | 60.8 | 55.8 | 49.7 | 45 | 44.5 | 42.4 | 43.2 | 38.8 | 36.5 | 33.5 | 30.7
| Tapper Position #2 | E-544 | 77.1 | 78.4 | 72.1 | 72 | 74.3 | 71.5 | 67.1 | 62.5 | 54.8 | 49 | 45.8 | 48.4 | 45.5 | 45.2 | 40.8 | 37.1 | 32.5 | 30.1
| Tapper Position #3 | E-545 | 77.9 | 79.6 | 72.1 | 72.5 | 74.1 | 71.2 | 66.9 | 61.2 | 53.5 | 46.6 | 43.6 | 45.4 | 42.9 | 44.3 | 39.9 | 36.9 | 33 | 29.8
| Tapper Position #4 | E-546 | 73.3 | 79.2 | 76.8 | 75.1 | 72.1 | 71.1 | 68.4 | 62.2 | 52.7 | 47.9 | 43 | 44.7 | 44.5 | 44.8 | 39 | 35.4 | 31.6 | 28.8
| Avg. Tapper Level |  | 77.1343 | 79.2542 | 74.4405 | 73.2985 | 74.3396 | 71.6117 | 67.6444 | 61.7307 | 54.3627 | 48.4529 | 44.491 | 46.0625 | 44.0029 | 44.4374 | 39.6993 | 36.5226 | 32.7055 | 29.9031
| Tapper w. Carpet | E-549 | 75.1 | 73.8 | 67.8 | 64.4 | 62.7 | 56.4 | 48.5 | 42.8 | 37.6 | 35.7 | 33.8 | 35.9 | 33.8 | 35.2 | 31.6 | 29.8 | 26.9 | 24.6
| Tapper Source Room | D-526 | 73.5 | 81.9 | 80.8 | 78.1 | 80.3 | 80.4 | 79.5 | 76.3 | 74.8 | 73.7 | 73.1 | 73.9 | 70.7 | 67.8 | 66 | 66.8 | 65.2 | 64.3
ASTC / NIC Calcs
ASTC Calc | Absorption (Sabines) |  | 313.1959 | 228.7818 | 305.877 | 194.3453 | 189.1119 | 170.1553 | 143.907 | 153.3155 | 169.5615 | 173.0972 | 150.3217 | 132.6084 | 127.4604 | 132.452 | 138.9423 | 137.9447 | 139.4495 | 147.0524
| Corr. Receiver |  | 78.2 | 79.5 | 73 | 65.6 | 61.6 | 57.6 | 52.7 | 47.5 | 42 | 39.9196 | 33.6622 | 30.4 | 28.2 | 25.5 | 22.1 | 19.6 | 17.7 | 16.1
| ATL |  | 19 | 18.2 | 19.9 | 27.8 | 33.5 | 36.1 | 40.8 | 41.7 | 44.5 | 48.5 | 53.9 | 58.5 | 58.5 | 59.4 | 65.2 | 69.3 | 72.2 | 72.8
| STC Contour |  |  | 25 | 28 | 31 | 34 | 37 | 40 | 41 | 42 | 43 | 44 | 45 | 45 | 45 | 45 | 45 | 45
| Deficiencies |  |  | 7 | 8 | 3 | 1 | 1 | -1 | -1 | -3 | -6 | -10 | -14 | -14 | -14 | -20 | -24 | -27 |  | 8 | << Maximum, Single Deficiency
| Positive Deficiencies |  |  | 7 | 8 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | << Sum of Positive Deficiencies
| 5 dB Back Check |  | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | fail | fail | fail | fail | fail | fail | fail
| Room Absorption Check |  |  | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass
NIC Calc | Corrected Receiver |  | 78.2 | 79.5 | 73 | 65.6 | 61.6 | 57.6 | 52.7 | 47.5 | 42 | 39.9196 | 33.6622 | 30.4 | 28.2 | 25.5 | 22.1 | 19.6 | 17.7 | 16.1
| NR |  | 17.6 | 15.5 | 18.4 | 24.4 | 30 | 32.1 | 36.1 | 37.2 | 40.5 | 44.6 | 49.3 | 53.4 | 53.2 | 54.3 | 60.3 | 64.4 | 67.3 | 68.2
| NIC Contour |  |  | 23 | 26 | 29 | 32 | 35 | 38 | 39 | 40 | 41 | 42 | 43 | 43 | 43 | 43 | 43 | 43
| Deficiencies |  |  | 8 | 8 | 5 | 2 | 3 | 2 | 2 | -1 | -4 | -7 | -10 | -10 | -11 | -17 | -21 | -24 |  | 8 | << Maximum, Single Deficiency
| Positive Deficiencies |  |  | 8 | 8 | 5 | 2 | 3 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | << Sum of Positive Deficiencies
|  |  | 1.4 | 2.7 | 1.5 | 3.4 | 3.5 | 4 | 4.7 | 4.5 | 4 | 3.9 | 4.6 | 5.1 | 5.3 | 5.1 | 4.9 | 4.9 | 4.9 | 4.6
AIIC Calcs
AIIC Calc | Absorption (Sabines) |  | 313.1959 | 228.7818 | 305.877 | 194.3453 | 189.1119 | 170.1553 | 143.907 | 153.3155 | 169.5615 | 173.0972 | 150.3217 | 132.6084 | 127.4604 | 132.452 | 138.9423 | 137.9447 | 139.4495 | 147.0524
| Corrected Receiver (ISPL) |  | 77.134 | 79.2538 | 74.4402 | 73.2975 | 74.3392 | 71.611 | 67.6428 | 61.7255 | 54.3417 | 48.3812 | 44.3479 | 45.9783 | 43.8788 | 44.3888 | 39.6455 | 36.4536 | 32.5693 | 29.757
| Normalized Receiver (ANISPL) |  | 82 | 83 | 79 | 76 | 77 | 74 | 69 | 63 | 56 | 50 | 46 | 47 | 45 | 45 | 41 | 38 | 34 | 31
| IIC Contour |  | 74 | 74 | 74 | 74 | 74 | 74 | 73 | 72 | 71 | 70 | 69 | 66 | 63 | 60 | 57 | 54
| Deficiencies |  | 8 | 9 | 5 | 2 | 3 | 0 | -4 | -9 | -15 | -20 | -23 | -19 | -18 | -15 | -16 | -16 |  |  | 9 | << Maximum Deficiency
| Positive Deficiencies |  | 8 | 9 | 5 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 27 | << Sum of Positive Deficiencies
| Absorption Check |  | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass
| 5 dB Back Check |  | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass
AIIC: Leg Flanking | Corrected Receiver |  | 77.134 | 79.2538 | 74.4402 | 73.2975 | 74.3392 | 71.611 | 67.6428 | 61.7255 | 54.3417 | 48.3812 | 44.3479 | 45.9783 | 43.8788 | 44.3888 | 39.6455 | 36.4536
| Tapper w. Carpet |  | 75.1 | 73.8 | 67.8 | 64.4 | 62.7 | 56.4 | 48.5 | 42.8 | 37.6 | 35.7 | 33.8 | 35.9 | 33.8 | 35.2 | 31.6 | 29.8
| Corrected Tapper w. Carpet |  | 75.0995 | 73.7985 | 67.7986 | 64.3919 | 62.6936 | 56.3766 | 48.3668 | 42.3745 | 36.4701 | 34.0946 | 31.8 | 34.9335 | 32.2811 | 34.7745 | 31.2406 | 29.4655
| "Corr. RX" - "Corr. Tapper w. Carpet" |  | 2.0344 | 5.4553 | 6.6417 | 8.9056 | 11.6456 | 15.2344 | 19.276 | 19.351 | 17.8716 | 14.2866 | 12.5479 | 11.0448 | 11.5976 | 9.6143 | 8.405 | 6.9881
| Flanking via Legs? |  | fail | fail | fail | fail | pass | pass | pass | pass | pass | pass | pass | pass | pass | fail | fail | fail | NOT REPORTED.
| "Tapper w. Carpet" - Background |  | 39.7 | 34.6 | 34.8 | 27.3 | 28.3 | 22.7 | 15.2 | 10.3 | 6.4 | 5.1 | 4.2 | 7 | 5.3 | 10.3 | 11 | 11.3
AIIC: Airborne Flanking | Pink Noise Source Room |  | 95.8 | 95 | 91.4 | 90 | 91.6 | 89.7 | 88.8 | 84.7 | 82.5 | 84.5 | 83 | 83.8 | 81.4 | 79.8 | 82.4 | 84
| Pink Noise Receiver Room |  | 78.2 | 79.5 | 73 | 65.6 | 61.6 | 57.6 | 52.7 | 47.5 | 42 | 40.4 | 35.1 | 32.4 | 30.2 | 27.5 | 24.1 | 21.6
| Corrected Receiver |  | 78.1998 | 79.4996 | 72.9996 | 65.5939 | 61.5917 | 57.5823 | 52.6498 | 47.3604 | 41.6229 | 39.9196 | 33.6622 | 30.4 | 28.2 | 25.5 | 22.1 | 19.6
| NR |  | 17.6002 | 15.5004 | 18.4004 | 24.4061 | 30.0083 | 32.1177 | 36.1502 | 37.3396 | 40.8771 | 44.5804 | 49.3378 | 53.4 | 53.2 | 54.3 | 60.3 | 64.4
| Tapper Source Room |  | 73.5 | 81.9 | 80.8 | 78.1 | 80.3 | 80.4 | 79.5 | 76.3 | 74.8 | 73.7 | 73.1 | 73.9 | 70.7 | 67.8 | 66 | 66.8
| "Tapper Source Room" - "NR" |  | 55.8998 | 66.3996 | 62.3996 | 53.6939 | 50.2917 | 48.2823 | 43.3498 | 38.9604 | 33.9229 | 29.1196 | 23.7622 | 20.5 | 17.5 | 13.5 | 5.7 | 2.4
| "Avg. Tapper Level" - Abv |  | 21.2345 | 12.8546 | 12.041 | 19.6047 | 24.0479 | 23.3294 | 24.2946 | 22.7702 | 20.4398 | 19.3333 | 20.7288 | 25.5625 | 26.5029 | 30.9374 | 33.9993 | 34.1226
| Airborne Flanking? |  | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass | pass
ISR Calc | Corrected Receiver (ISPL) |  | 77.134 | 79.2538 | 74.4402 | 73.2975 | 74.3392 | 71.611 | 67.6428 | 61.7255 | 54.3417 | 48.3812 | 44.3479 | 45.9783 | 43.8788 | 44.3888 | 39.6455 | 36.4536 | 32.5693 | 29.757
| IIC Contour |  | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 68 | 67 | 66 | 65 | 62 | 59 | 56 | 53 | 50
| Deficiencies |  | 7 | 9 | 4 | 3 | 4 | 2 | -1 | -6 | -13 | -18 | -21 | -16 | -15 | -12 | -13 | -14 |  |  | 9 | << Maximum Deficiency
| Positive Deficiencies |  | 7 | 9 | 4 | 3 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 29 | << Sum of Positive Deficiencies
| 5 dB Back Check |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ASTC/AIIC Explanation
was calculated. The ASTC rating is based on Apparent Transmission Loss (ATL), and includes the effects of noise flanking. The ASTC reference contour is shown on the next page, and has been “fit” to the Apparent Transmission Loss values, in accordance with the procedure of
was calculated. The NIC rating is based on Noise Reduction (NR), and includes the effects of noise flanking. The NIC reference contour is shown on the next page, and has been “fit” to the Apparent Transmission Loss values, in accordance with the procedure of
was calculated. The AIIC rating is based on Absorption Normalized Impact Sound Pressure Level (ANISPL), and includes the effects of noise flanking. The AIIC reference contour is shown on the next page, and has been “fit” to the ANISPL values, in accordance with the procedure of
was calculated. The ISR rating is based on Impact Sound Pressure Level (ISPL), and includes the effects of noise flanking. The ISR reference contour is shown on the next page, and has been “fit” to the ISPL values, in accordance with the procedure of
, with all exceptions noted below. The requirements for measuring and reporting Apparent Transmission Loss (ATL) and Apparent Sound Transmission Class (ASTC) were not met, therefore only Noise Reduction (NR) and Noise Isolation Class (NIC) have been reported. Exceptions to
, with all exceptions noted below. The requirements for measuring and reporting Absorption Normalized Impact Sound Pressure Levels (ANISPL) and Apparent Impact Insulation Class (AIIC) were not met, therefore only Impact Sound Pressure Level (ISPL) and Impact Sound Rating (ISR) have been reported. Exceptions to

## equipment
Equipment Type | Manufacturer | Model Number | Serial Number | Last NIST Traceable Calibration | Last Local Calibration
SLM D | Larson Davis | 831 | 3784 | 44823 | 45027
Preamp | Larson Davis | PRM831 | 51188 | 44823 | 45027
Mic | Larson Davis | 377B20 | 301698 | 44820 | 45027
SLM E | Larson Davis | 831 | 4328 | 44858 | 45027
Preamp | Larson Davis | PRM831 | 046469 | 44858 | 45027
Mic | Larson Davis | 377B20 | 168830 | 44854 | 45027
Calibrator (E) | Larson Davis | CAL200 | 5955 | 44860 | N/A
Calibrator (D) | Larson Davis | CAL200 | 2775671 | 44823 | N/A
Amplified Loudspeakers (QTY 2) | QSC | K10 | GAA530909 | N/A | N/A
Noise Generator: | NTi Audio | MR-PRO | 0162 | N/A | N/A

## dynamic calculation
ATL | 19 | 18.2 | 19.9 | 27.8 | 33.5 | 36.1 | 40.8 | 41.7 | 44.5 | 48.5 | 53.9 | 58.5 | 58.5 | 59.4 | 65.2 | 69.3 | 72.2 | 72.8 | 28 | 26 | 41
STC | [18 empty] | Sum | max def | STC Deficiencies
Contour | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 |  |  | Contour | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000
16 |  | 0 | 3 | 6 | 9 | 12 | 15 | 16 | 17 | 18 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | -17 | 16 |  | -18 | -17 | -22 | -25 | -24 | -26 | -26 | -28 | -31 | -35 | -39 | -39 | -39 | -45 | -49 | -52 | -53
17 |  | 1 | 4 | 7 | 10 | 13 | 16 | 17 | 18 | 19 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | -16 | 17 |  | -17 | -16 | -21 | -24 | -23 | -25 | -25 | -27 | -30 | -34 | -38 | -38 | -38 | -44 | -48 | -51 | -52
18 |  | 2 | 5 | 8 | 11 | 14 | 17 | 18 | 19 | 20 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | -15 | 18 |  | -16 | -15 | -20 | -23 | -22 | -24 | -24 | -26 | -29 | -33 | -37 | -37 | -37 | -43 | -47 | -50 | -51
19 |  | 3 | 6 | 9 | 12 | 15 | 18 | 19 | 20 | 21 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0 | -14 | 19 |  | -15 | -14 | -19 | -22 | -21 | -23 | -23 | -25 | -28 | -32 | -36 | -36 | -36 | -42 | -46 | -49 | -50
20 |  | 4 | 7 | 10 | 13 | 16 | 19 | 20 | 21 | 22 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | -13 | 20 |  | -14 | -13 | -18 | -21 | -20 | -22 | -22 | -24 | -27 | -31 | -35 | -35 | -35 | -41 | -45 | -48 | -49
21 |  | 5 | 8 | 11 | 14 | 17 | 20 | 21 | 22 | 23 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | -12 | 21 |  | -13 | -12 | -17 | -20 | -19 | -21 | -21 | -23 | -26 | -30 | -34 | -34 | -34 | -40 | -44 | -47 | -48
22 |  | 6 | 9 | 12 | 15 | 18 | 21 | 22 | 23 | 24 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 0 | -11 | 22 |  | -12 | -11 | -16 | -19 | -18 | -20 | -20 | -22 | -25 | -29 | -33 | -33 | -33 | -39 | -43 | -46 | -47
23 |  | 7 | 10 | 13 | 16 | 19 | 22 | 23 | 24 | 25 | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 0 | -10 | 23 |  | -11 | -10 | -15 | -18 | -17 | -19 | -19 | -21 | -24 | -28 | -32 | -32 | -32 | -38 | -42 | -45 | -46
24 |  | 8 | 11 | 14 | 17 | 20 | 23 | 24 | 25 | 26 | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 0 | -9 | 24 |  | -10 | -9 | -14 | -17 | -16 | -18 | -18 | -20 | -23 | -27 | -31 | -31 | -31 | -37 | -41 | -44 | -45
25 |  | 9 | 12 | 15 | 18 | 21 | 24 | 25 | 26 | 27 | 28 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 0 | -8 | 25 |  | -9 | -8 | -13 | -16 | -15 | -17 | -17 | -19 | -22 | -26 | -30 | -30 | -30 | -36 | -40 | -43 | -44
26 |  | 10 | 13 | 16 | 19 | 22 | 25 | 26 | 27 | 28 | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | -7 | 26 |  | -8 | -7 | -12 | -15 | -14 | -16 | -16 | -18 | -21 | -25 | -29 | -29 | -29 | -35 | -39 | -42 | -43
27 |  | 11 | 14 | 17 | 20 | 23 | 26 | 27 | 28 | 29 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 0 | -6 | 27 |  | -7 | -6 | -11 | -14 | -13 | -15 | -15 | -17 | -20 | -24 | -28 | -28 | -28 | -34 | -38 | -41 | -42
28 |  | 12 | 15 | 18 | 21 | 24 | 27 | 28 | 29 | 30 | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 0 | -5 | 28 |  | -6 | -5 | -10 | -13 | -12 | -14 | -14 | -16 | -19 | -23 | -27 | -27 | -27 | -33 | -37 | -40 | -41
29 |  | 13 | 16 | 19 | 22 | 25 | 28 | 29 | 30 | 31 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | -4 | 29 |  | -5 | -4 | -9 | -12 | -11 | -13 | -13 | -15 | -18 | -22 | -26 | -26 | -26 | -32 | -36 | -39 | -40
30 |  | 14 | 17 | 20 | 23 | 26 | 29 | 30 | 31 | 32 | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 0 | -3 | 30 |  | -4 | -3 | -8 | -11 | -10 | -12 | -12 | -14 | -17 | -21 | -25 | -25 | -25 | -31 | -35 | -38 | -39
31 |  | 15 | 18 | 21 | 24 | 27 | 30 | 31 | 32 | 33 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | -2 | 31 |  | -3 | -2 | -7 | -10 | -9 | -11 | -11 | -13 | -16 | -20 | -24 | -24 | -24 | -30 | -34 | -37 | -38
32 |  | 16 | 19 | 22 | 25 | 28 | 31 | 32 | 33 | 34 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 0 | -1 | 32 |  | -2 | -1 | -6 | -9 | -8 | -10 | -10 | -12 | -15 | -19 | -23 | -23 | -23 | -29 | -33 | -36 | -37
33 |  | 17 | 20 | 23 | 26 | 29 | 32 | 33 | 34 | 35 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 0 | 0 | 33 |  | -1 | 0 | -5 | -8 | -7 | -9 | -9 | -11 | -14 | -18 | -22 | -22 | -22 | -28 | -32 | -35 | -36
34 |  | 18 | 21 | 24 | 27 | 30 | 33 | 34 | 35 | 36 | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 1 | 1 | 34 |  | 0 | 1 | -4 | -7 | -6 | -8 | -8 | -10 | -13 | -17 | -21 | -21 | -21 | -27 | -31 | -34 | -35
35 |  | 19 | 22 | 25 | 28 | 31 | 34 | 35 | 36 | 37 | 38 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 3 | 2 | 35 |  | 1 | 2 | -3 | -6 | -5 | -7 | -7 | -9 | -12 | -16 | -20 | -20 | -20 | -26 | -30 | -33 | -34
36 |  | 20 | 23 | 26 | 29 | 32 | 35 | 36 | 37 | 38 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 5 | 3 | 36 |  | 2 | 3 | -2 | -5 | -4 | -6 | -6 | -8 | -11 | -15 | -19 | -19 | -19 | -25 | -29 | -32 | -33
37 |  | 21 | 24 | 27 | 30 | 33 | 36 | 37 | 38 | 39 | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 7 | 4 | 37 |  | 3 | 4 | -1 | -4 | -3 | -5 | -5 | -7 | -10 | -14 | -18 | -18 | -18 | -24 | -28 | -31 | -32
38 |  | 22 | 25 | 28 | 31 | 34 | 37 | 38 | 39 | 40 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 9 | 5 | 38 |  | 4 | 5 | 0 | -3 | -2 | -4 | -4 | -6 | -9 | -13 | -17 | -17 | -17 | -23 | -27 | -30 | -31
39 |  | 23 | 26 | 29 | 32 | 35 | 38 | 39 | 40 | 41 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 12 | 6 | 39 |  | 5 | 6 | 1 | -2 | -1 | -3 | -3 | -5 | -8 | -12 | -16 | -16 | -16 | -22 | -26 | -29 | -30
40 |  | 24 | 27 | 30 | 33 | 36 | 39 | 40 | 41 | 42 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 15 | 7 | 40 |  | 6 | 7 | 2 | -1 | 0 | -2 | -2 | -4 | -7 | -11 | -15 | -15 | -15 | -21 | -25 | -28 | -29
41 |  | 25 | 28 | 31 | 34 | 37 | 40 | 41 | 42 | 43 | 44 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 20 | 8 | 41 |  | 7 | 8 | 3 | 1 | 1 | -1 | -1 | -3 | -6 | -10 | -14 | -14 | -14 | -20 | -24 | -27 | -28
42 |  | 26 | 29 | 32 | 35 | 38 | 41 | 42 | 43 | 44 | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 25 | 9 | 42 |  | 8 | 9 | 4 | 2 | 2 | 0 | 0 | -2 | -5 | -9 | -13 | -13 | -13 | -19 | -23 | -26 | -27
43 |  | 27 | 30 | 33 | 36 | 39 | 42 | 43 | 44 | 45 | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 32 | 10 | 43 |  | 9 | 10 | 5 | 3 | 3 | 1 | 1 | -1 | -4 | -8 | -12 | -12 | -12 | -18 | -22 | -25 | -26
44 |  | 28 | 31 | 34 | 37 | 40 | 43 | 44 | 45 | 46 | 47 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 40 | 11 | 44 |  | 10 | 11 | 6 | 4 | 4 | 2 | 2 | 1 | -3 | -7 | -11 | -11 | -11 | -17 | -21 | -24 | -25
45 |  | 29 | 32 | 35 | 38 | 41 | 44 | 45 | 46 | 47 | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 12 | 45 |  | 11 | 12 | 7 | 5 | 5 | 3 | 3 | 2 | -2 | -6 | -10 | -10 | -10 | -16 | -20 | -23 | -24
46 |  | 30 | 33 | 36 | 39 | 42 | 45 | 46 | 47 | 48 | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 13 | 46 |  | 12 | 13 | 8 | 6 | 6 | 4 | 4 | 3 | -1 | -5 | -9 | -9 | -9 | -15 | -19 | -22 | -23
47 |  | 31 | 34 | 37 | 40 | 43 | 46 | 47 | 48 | 49 | 50 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 65 | 14 | 47 |  | 13 | 14 | 9 | 7 | 7 | 5 | 5 | 4 | 1 | -4 | -8 | -8 | -8 | -14 | -18 | -21 | -22
48 |  | 32 | 35 | 38 | 41 | 44 | 47 | 48 | 49 | 50 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 74 | 15 | 48 |  | 14 | 15 | 10 | 8 | 8 | 6 | 6 | 5 | 2 | -3 | -7 | -7 | -7 | -13 | -17 | -20 | -21
49 |  | 33 | 36 | 39 | 42 | 45 | 48 | 49 | 50 | 51 | 52 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 83 | 16 | 49 |  | 15 | 16 | 11 | 9 | 9 | 7 | 7 | 6 | 3 | -2 | -6 | -6 | -6 | -12 | -16 | -19 | -20
50 |  | 34 | 37 | 40 | 43 | 46 | 49 | 50 | 51 | 52 | 53 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 92 | 17 | 50 |  | 16 | 17 | 12 | 10 | 10 | 8 | 8 | 7 | 4 | -1 | -5 | -5 | -5 | -11 | -15 | -18 | -19
51 |  | 35 | 38 | 41 | 44 | 47 | 50 | 51 | 52 | 53 | 54 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 101 | 18 | 51 |  | 17 | 18 | 13 | 11 | 11 | 9 | 9 | 8 | 5 | 0 | -4 | -4 | -4 | -10 | -14 | -17 | -18
52 |  | 36 | 39 | 42 | 45 | 48 | 51 | 52 | 53 | 54 | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 111 | 19 | 52 |  | 18 | 19 | 14 | 12 | 12 | 10 | 10 | 9 | 6 | 1 | -3 | -3 | -3 | -9 | -13 | -16 | -17
53 |  | 37 | 40 | 43 | 46 | 49 | 52 | 53 | 54 | 55 | 56 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 121 | 20 | 53 |  | 19 | 20 | 15 | 13 | 13 | 11 | 11 | 10 | 7 | 2 | -2 | -2 | -2 | -8 | -12 | -15 | -16
54 |  | 38 | 41 | 44 | 47 | 50 | 53 | 54 | 55 | 56 | 57 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 131 | 21 | 54 |  | 20 | 21 | 16 | 14 | 14 | 12 | 12 | 11 | 8 | 3 | -1 | -1 | -1 | -7 | -11 | -14 | -15
55 |  | 39 | 42 | 45 | 48 | 51 | 54 | 55 | 56 | 57 | 58 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 143 | 22 | 55 |  | 21 | 22 | 17 | 15 | 15 | 13 | 13 | 12 | 9 | 4 | 1 | 1 | 0 | -6 | -10 | -13 | -14
56 |  | 40 | 43 | 46 | 49 | 52 | 55 | 56 | 57 | 58 | 59 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 156 | 23 | 56 |  | 22 | 23 | 18 | 16 | 16 | 14 | 14 | 13 | 10 | 5 | 2 | 2 | 1 | -5 | -9 | -12 | -13
57 |  | 41 | 44 | 47 | 50 | 53 | 56 | 57 | 58 | 59 | 60 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 169 | 24 | 57 |  | 23 | 24 | 19 | 17 | 17 | 15 | 15 | 14 | 11 | 6 | 3 | 3 | 2 | -4 | -8 | -11 | -12
58 |  | 42 | 45 | 48 | 51 | 54 | 57 | 58 | 59 | 60 | 61 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 182 | 25 | 58 |  | 24 | 25 | 20 | 18 | 18 | 16 | 16 | 15 | 12 | 7 | 4 | 4 | 3 | -3 | -7 | -10 | -11
59 |  | 43 | 46 | 49 | 52 | 55 | 58 | 59 | 60 | 61 | 62 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 195 | 26 | 59 |  | 25 | 26 | 21 | 19 | 19 | 17 | 17 | 16 | 13 | 8 | 5 | 5 | 4 | -2 | -6 | -9 | -10
60 |  | 44 | 47 | 50 | 53 | 56 | 59 | 60 | 61 | 62 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 208 | 27 | 60 |  | 26 | 27 | 22 | 20 | 20 | 18 | 18 | 17 | 14 | 9 | 6 | 6 | 5 | -1 | -5 | -8 | -9
61 |  | 45 | 48 | 51 | 54 | 57 | 60 | 61 | 62 | 63 | 64 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 221 | 28 | 61 |  | 27 | 28 | 23 | 21 | 21 | 19 | 19 | 18 | 15 | 10 | 7 | 7 | 6 | 0 | -4 | -7 | -8
62 |  | 46 | 49 | 52 | 55 | 58 | 61 | 62 | 63 | 64 | 65 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 235 | 29 | 62 |  | 28 | 29 | 24 | 22 | 22 | 20 | 20 | 19 | 16 | 11 | 8 | 8 | 7 | 1 | -3 | -6 | -7
63 |  | 47 | 50 | 53 | 56 | 59 | 62 | 63 | 64 | 65 | 66 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 249 | 30 | 63 |  | 29 | 30 | 25 | 23 | 23 | 21 | 21 | 20 | 17 | 12 | 9 | 9 | 8 | 2 | -2 | -5 | -6
64 |  | 48 | 51 | 54 | 57 | 60 | 63 | 64 | 65 | 66 | 67 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 263 | 31 | 64 |  | 30 | 31 | 26 | 24 | 24 | 22 | 22 | 21 | 18 | 13 | 10 | 10 | 9 | 3 | -1 | -4 | -5
65 |  | 49 | 52 | 55 | 58 | 61 | 64 | 65 | 66 | 67 | 68 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 277 | 32 | 65 |  | 31 | 32 | 27 | 25 | 25 | 23 | 23 | 22 | 19 | 14 | 11 | 11 | 10 | 4 | 0 | -3 | -4
66 |  | 50 | 53 | 56 | 59 | 62 | 65 | 66 | 67 | 68 | 69 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 292 | 33 | 66 |  | 32 | 33 | 28 | 26 | 26 | 24 | 24 | 23 | 20 | 15 | 12 | 12 | 11 | 5 | 1 | -2 | -3
67 |  | 51 | 54 | 57 | 60 | 63 | 66 | 67 | 68 | 69 | 70 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 307 | 34 | 67 |  | 33 | 34 | 29 | 27 | 27 | 25 | 25 | 24 | 21 | 16 | 13 | 13 | 12 | 6 | 2 | -1 | -2
68 |  | 52 | 55 | 58 | 61 | 64 | 67 | 68 | 69 | 70 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 322 | 35 | 68 |  | 34 | 35 | 30 | 28 | 28 | 26 | 26 | 25 | 22 | 17 | 14 | 14 | 13 | 7 | 3 | 0 | -1
69 |  | 53 | 56 | 59 | 62 | 65 | 68 | 69 | 70 | 71 | 72 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 338 | 36 | 69 |  | 35 | 36 | 31 | 29 | 29 | 27 | 27 | 26 | 23 | 18 | 15 | 15 | 14 | 8 | 4 | 1 | 0
70 |  | 54 | 57 | 60 | 63 | 66 | 69 | 70 | 71 | 72 | 73 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 354 | 37 | 70 |  | 36 | 37 | 32 | 30 | 30 | 28 | 28 | 27 | 24 | 19 | 16 | 16 | 15 | 9 | 5 | 2 | 1
71 |  | 55 | 58 | 61 | 64 | 67 | 70 | 71 | 72 | 73 | 74 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 370 | 38 | 71 |  | 37 | 38 | 33 | 31 | 31 | 29 | 29 | 28 | 25 | 20 | 17 | 17 | 16 | 10 | 6 | 3 | 2
72 |  | 56 | 59 | 62 | 65 | 68 | 71 | 72 | 73 | 74 | 75 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 386 | 39 | 72 |  | 38 | 39 | 34 | 32 | 32 | 30 | 30 | 29 | 26 | 21 | 18 | 18 | 17 | 11 | 7 | 4 | 3
73 |  | 57 | 60 | 63 | 66 | 69 | 72 | 73 | 74 | 75 | 76 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 402 | 40 | 73 |  | 39 | 40 | 35 | 33 | 33 | 31 | 31 | 30 | 27 | 22 | 19 | 19 | 18 | 12 | 8 | 5 | 4
74 |  | 58 | 61 | 64 | 67 | 70 | 73 | 74 | 75 | 76 | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 418 | 41 | 74 |  | 40 | 41 | 36 | 34 | 34 | 32 | 32 | 31 | 28 | 23 | 20 | 20 | 19 | 13 | 9 | 6 | 5
75 |  | 59 | 62 | 65 | 68 | 71 | 74 | 75 | 76 | 77 | 78 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 434 | 42 | 75 |  | 41 | 42 | 37 | 35 | 35 | 33 | 33 | 32 | 29 | 24 | 21 | 21 | 20 | 14 | 10 | 7 | 6
76 |  | 60 | 63 | 66 | 69 | 72 | 75 | 76 | 77 | 78 | 79 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 450 | 43 | 76 |  | 42 | 43 | 38 | 36 | 36 | 34 | 34 | 33 | 30 | 25 | 22 | 22 | 21 | 15 | 11 | 8 | 7
77 |  | 61 | 64 | 67 | 70 | 73 | 76 | 77 | 78 | 79 | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 466 | 44 | 77 |  | 43 | 44 | 39 | 37 | 37 | 35 | 35 | 34 | 31 | 26 | 23 | 23 | 22 | 16 | 12 | 9 | 8
78 |  | 62 | 65 | 68 | 71 | 74 | 77 | 78 | 79 | 80 | 81 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 482 | 45 | 78 |  | 44 | 45 | 40 | 38 | 38 | 36 | 36 | 35 | 32 | 27 | 24 | 24 | 23 | 17 | 13 | 10 | 9
79 |  | 63 | 66 | 69 | 72 | 75 | 78 | 79 | 80 | 81 | 82 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 498 | 46 | 79 |  | 45 | 46 | 41 | 39 | 39 | 37 | 37 | 36 | 33 | 28 | 25 | 25 | 24 | 18 | 14 | 11 | 10
80 |  | 64 | 67 | 70 | 73 | 76 | 79 | 80 | 81 | 82 | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 514 | 47 | 80 |  | 46 | 47 | 42 | 40 | 40 | 38 | 38 | 37 | 34 | 29 | 26 | 26 | 25 | 19 | 15 | 12 | 11
81 |  | 65 | 68 | 71 | 74 | 77 | 80 | 81 | 82 | 83 | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 530 | 48 | 81 |  | 47 | 48 | 43 | 41 | 41 | 39 | 39 | 38 | 35 | 30 | 27 | 27 | 26 | 20 | 16 | 13 | 12
82 |  | 66 | 69 | 72 | 75 | 78 | 81 | 82 | 83 | 84 | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 546 | 49 | 82 |  | 48 | 49 | 44 | 42 | 42 | 40 | 40 | 39 | 36 | 31 | 28 | 28 | 27 | 21 | 17 | 14 | 13
83 |  | 67 | 70 | 73 | 76 | 79 | 82 | 83 | 84 | 85 | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 562 | 50 | 83 |  | 49 | 50 | 45 | 43 | 43 | 41 | 41 | 40 | 37 | 32 | 29 | 29 | 28 | 22 | 18 | 15 | 14
84 |  | 68 | 71 | 74 | 77 | 80 | 83 | 84 | 85 | 86 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 578 | 51 | 84 |  | 50 | 51 | 46 | 44 | 44 | 42 | 42 | 41 | 38 | 33 | 30 | 30 | 29 | 23 | 19 | 16 | 15
85 |  | 69 | 72 | 75 | 78 | 81 | 84 | 85 | 86 | 87 | 88 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 594 | 52 | 85 |  | 51 | 52 | 47 | 45 | 45 | 43 | 43 | 42 | 39 | 34 | 31 | 31 | 30 | 24 | 20 | 17 | 16
86 |  | 70 | 73 | 76 | 79 | 82 | 85 | 86 | 87 | 88 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 610 | 53 | 86 |  | 52 | 53 | 48 | 46 | 46 | 44 | 44 | 43 | 40 | 35 | 32 | 32 | 31 | 25 | 21 | 18 | 17
87 |  | 71 | 74 | 77 | 80 | 83 | 86 | 87 | 88 | 89 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 626 | 54 | 87 |  | 53 | 54 | 49 | 47 | 47 | 45 | 45 | 44 | 41 | 36 | 33 | 33 | 32 | 26 | 22 | 19 | 18
88 |  | 72 | 75 | 78 | 81 | 84 | 87 | 88 | 89 | 90 | 91 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 642 | 55 | 88 |  | 54 | 55 | 50 | 48 | 48 | 46 | 46 | 45 | 42 | 37 | 34 | 34 | 33 | 27 | 23 | 20 | 19
89 |  | 73 | 76 | 79 | 82 | 85 | 88 | 89 | 90 | 91 | 92 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 658 | 56 | 89 |  | 55 | 56 | 51 | 49 | 49 | 47 | 47 | 46 | 43 | 38 | 35 | 35 | 34 | 28 | 24 | 21 | 20
90 |  | 74 | 77 | 80 | 83 | 86 | 89 | 90 | 91 | 92 | 93 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 674 | 57 | 90 |  | 56 | 57 | 52 | 50 | 50 | 48 | 48 | 47 | 44 | 39 | 36 | 36 | 35 | 29 | 25 | 22 | 21
91 |  | 75 | 78 | 81 | 84 | 87 | 90 | 91 | 92 | 93 | 94 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 690 | 58 | 91 |  | 57 | 58 | 53 | 51 | 51 | 49 | 49 | 48 | 45 | 40 | 37 | 37 | 36 | 30 | 26 | 23 | 22
92 |  | 76 | 79 | 82 | 85 | 88 | 91 | 92 | 93 | 94 | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 706 | 59 | 92 |  | 58 | 59 | 54 | 52 | 52 | 50 | 50 | 49 | 46 | 41 | 38 | 38 | 37 | 31 | 27 | 24 | 23
93 |  | 77 | 80 | 83 | 86 | 89 | 92 | 93 | 94 | 95 | 96 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 722 | 60 | 93 |  | 59 | 60 | 55 | 53 | 53 | 51 | 51 | 50 | 47 | 42 | 39 | 39 | 38 | 32 | 28 | 25 | 24
94 |  | 78 | 81 | 84 | 87 | 90 | 93 | 94 | 95 | 96 | 97 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 738 | 61 | 94 |  | 60 | 61 | 56 | 54 | 54 | 52 | 52 | 51 | 48 | 43 | 40 | 40 | 39 | 33 | 29 | 26 | 25
95 |  | 79 | 82 | 85 | 88 | 91 | 94 | 95 | 96 | 97 | 98 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 754 | 62 | 95 |  | 61 | 62 | 57 | 55 | 55 | 53 | 53 | 52 | 49 | 44 | 41 | 41 | 40 | 34 | 30 | 27 | 26
96 |  | 80 | 83 | 86 | 89 | 92 | 95 | 96 | 97 | 98 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 770 | 63 | 96 |  | 62 | 63 | 58 | 56 | 56 | 54 | 54 | 53 | 50 | 45 | 42 | 42 | 41 | 35 | 31 | 28 | 27
97 |  | 81 | 84 | 87 | 90 | 93 | 96 | 97 | 98 | 99 | 100 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 786 | 64 | 97 |  | 63 | 64 | 59 | 57 | 57 | 55 | 55 | 54 | 51 | 46 | 43 | 43 | 42 | 36 | 32 | 29 | 28
98 |  | 82 | 85 | 88 | 91 | 94 | 97 | 98 | 99 | 100 | 101 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 802 | 65 | 98 |  | 64 | 65 | 60 | 58 | 58 | 56 | 56 | 55 | 52 | 47 | 44 | 44 | 43 | 37 | 33 | 30 | 29
99 |  | 83 | 86 | 89 | 92 | 95 | 98 | 99 | 100 | 101 | 102 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 818 | 66 | 99 |  | 65 | 66 | 61 | 59 | 59 | 57 | 57 | 56 | 53 | 48 | 45 | 45 | 44 | 38 | 34 | 31 | 30
100 |  | 84 | 87 | 90 | 93 | 96 | 99 | 100 | 101 | 102 | 103 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 834 | 67 | 100 |  | 66 | 67 | 62 | 60 | 60 | 58 | 58 | 57 | 54 | 49 | 46 | 46 | 45 | 39 | 35 | 32 | 31
NR | 17.6 | 15.5 | 18.4 | 24.4 | 30 | 32.1 | 36.1 | 37.2 | 40.5 | 44.6 | 49.3 | 53.4 | 53.2 | 54.3 | 60.3 | 64.4 | 67.3 | 68.2 | 24 | 24 | 39
NIC Contour | [18 empty] | Sum | max def | STC Deficiencies
Contour | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 |  |  | Contour | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000
16 |  | 0 | 3 | 6 | 9 | 12 | 15 | 16 | 17 | 18 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | -15 | 16 |  | -16 | -15 | -18 | -21 | -20 | -21 | -21 | -24 | -27 | -30 | -33 | -33 | -34 | -40 | -44 | -47 | -48
17 |  | 1 | 4 | 7 | 10 | 13 | 16 | 17 | 18 | 19 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | -14 | 17 |  | -15 | -14 | -17 | -20 | -19 | -20 | -20 | -23 | -26 | -29 | -32 | -32 | -33 | -39 | -43 | -46 | -47
18 |  | 2 | 5 | 8 | 11 | 14 | 17 | 18 | 19 | 20 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | -13 | 18 |  | -14 | -13 | -16 | -19 | -18 | -19 | -19 | -22 | -25 | -28 | -31 | -31 | -32 | -38 | -42 | -45 | -46
19 |  | 3 | 6 | 9 | 12 | 15 | 18 | 19 | 20 | 21 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0 | -12 | 19 |  | -13 | -12 | -15 | -18 | -17 | -18 | -18 | -21 | -24 | -27 | -30 | -30 | -31 | -37 | -41 | -44 | -45
20 |  | 4 | 7 | 10 | 13 | 16 | 19 | 20 | 21 | 22 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | -11 | 20 |  | -12 | -11 | -14 | -17 | -16 | -17 | -17 | -20 | -23 | -26 | -29 | -29 | -30 | -36 | -40 | -43 | -44
21 |  | 5 | 8 | 11 | 14 | 17 | 20 | 21 | 22 | 23 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | -10 | 21 |  | -11 | -10 | -13 | -16 | -15 | -16 | -16 | -19 | -22 | -25 | -28 | -28 | -29 | -35 | -39 | -42 | -43
22 |  | 6 | 9 | 12 | 15 | 18 | 21 | 22 | 23 | 24 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 0 | -9 | 22 |  | -10 | -9 | -12 | -15 | -14 | -15 | -15 | -18 | -21 | -24 | -27 | -27 | -28 | -34 | -38 | -41 | -42
23 |  | 7 | 10 | 13 | 16 | 19 | 22 | 23 | 24 | 25 | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 0 | -8 | 23 |  | -9 | -8 | -11 | -14 | -13 | -14 | -14 | -17 | -20 | -23 | -26 | -26 | -27 | -33 | -37 | -40 | -41
24 |  | 8 | 11 | 14 | 17 | 20 | 23 | 24 | 25 | 26 | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 0 | -7 | 24 |  | -8 | -7 | -10 | -13 | -12 | -13 | -13 | -16 | -19 | -22 | -25 | -25 | -26 | -32 | -36 | -39 | -40
25 |  | 9 | 12 | 15 | 18 | 21 | 24 | 25 | 26 | 27 | 28 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 0 | -6 | 25 |  | -7 | -6 | -9 | -12 | -11 | -12 | -12 | -15 | -18 | -21 | -24 | -24 | -25 | -31 | -35 | -38 | -39
26 |  | 10 | 13 | 16 | 19 | 22 | 25 | 26 | 27 | 28 | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | -5 | 26 |  | -6 | -5 | -8 | -11 | -10 | -11 | -11 | -14 | -17 | -20 | -23 | -23 | -24 | -30 | -34 | -37 | -38
27 |  | 11 | 14 | 17 | 20 | 23 | 26 | 27 | 28 | 29 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 0 | -4 | 27 |  | -5 | -4 | -7 | -10 | -9 | -10 | -10 | -13 | -16 | -19 | -22 | -22 | -23 | -29 | -33 | -36 | -37
28 |  | 12 | 15 | 18 | 21 | 24 | 27 | 28 | 29 | 30 | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 0 | -3 | 28 |  | -4 | -3 | -6 | -9 | -8 | -9 | -9 | -12 | -15 | -18 | -21 | -21 | -22 | -28 | -32 | -35 | -36
29 |  | 13 | 16 | 19 | 22 | 25 | 28 | 29 | 30 | 31 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | -2 | 29 |  | -3 | -2 | -5 | -8 | -7 | -8 | -8 | -11 | -14 | -17 | -20 | -20 | -21 | -27 | -31 | -34 | -35
30 |  | 14 | 17 | 20 | 23 | 26 | 29 | 30 | 31 | 32 | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 0 | -1 | 30 |  | -2 | -1 | -4 | -7 | -6 | -7 | -7 | -10 | -13 | -16 | -19 | -19 | -20 | -26 | -30 | -33 | -34
31 |  | 15 | 18 | 21 | 24 | 27 | 30 | 31 | 32 | 33 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 0 | 31 |  | -1 | 0 | -3 | -6 | -5 | -6 | -6 | -9 | -12 | -15 | -18 | -18 | -19 | -25 | -29 | -32 | -33
32 |  | 16 | 19 | 22 | 25 | 28 | 31 | 32 | 33 | 34 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 2 | 1 | 32 |  | 1 | 1 | -2 | -5 | -4 | -5 | -5 | -8 | -11 | -14 | -17 | -17 | -18 | -24 | -28 | -31 | -32
33 |  | 17 | 20 | 23 | 26 | 29 | 32 | 33 | 34 | 35 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 4 | 2 | 33 |  | 2 | 2 | -1 | -4 | -3 | -4 | -4 | -7 | -10 | -13 | -16 | -16 | -17 | -23 | -27 | -30 | -31
34 |  | 18 | 21 | 24 | 27 | 30 | 33 | 34 | 35 | 36 | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 6 | 3 | 34 |  | 3 | 3 | 0 | -3 | -2 | -3 | -3 | -6 | -9 | -12 | -15 | -15 | -16 | -22 | -26 | -29 | -30
35 |  | 19 | 22 | 25 | 28 | 31 | 34 | 35 | 36 | 37 | 38 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 9 | 4 | 35 |  | 4 | 4 | 1 | -2 | -1 | -2 | -2 | -5 | -8 | -11 | -14 | -14 | -15 | -21 | -25 | -28 | -29
36 |  | 20 | 23 | 26 | 29 | 32 | 35 | 36 | 37 | 38 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 12 | 5 | 36 |  | 5 | 5 | 2 | -1 | 0 | -1 | -1 | -4 | -7 | -10 | -13 | -13 | -14 | -20 | -24 | -27 | -28
37 |  | 21 | 24 | 27 | 30 | 33 | 36 | 37 | 38 | 39 | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 16 | 6 | 37 |  | 6 | 6 | 3 | 0 | 1 | 0 | 0 | -3 | -6 | -9 | -12 | -12 | -13 | -19 | -23 | -26 | -27
38 |  | 22 | 25 | 28 | 31 | 34 | 37 | 38 | 39 | 40 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 23 | 7 | 38 |  | 7 | 7 | 4 | 1 | 2 | 1 | 1 | -2 | -5 | -8 | -11 | -11 | -12 | -18 | -22 | -25 | -26
39 |  | 23 | 26 | 29 | 32 | 35 | 38 | 39 | 40 | 41 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 30 | 8 | 39 |  | 8 | 8 | 5 | 2 | 3 | 2 | 2 | -1 | -4 | -7 | -10 | -10 | -11 | -17 | -21 | -24 | -25
40 |  | 24 | 27 | 30 | 33 | 36 | 39 | 40 | 41 | 42 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 38 | 9 | 40 |  | 9 | 9 | 6 | 3 | 4 | 3 | 3 | 1 | -3 | -6 | -9 | -9 | -10 | -16 | -20 | -23 | -24
41 |  | 25 | 28 | 31 | 34 | 37 | 40 | 41 | 42 | 43 | 44 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 46 | 10 | 41 |  | 10 | 10 | 7 | 4 | 5 | 4 | 4 | 2 | -2 | -5 | -8 | -8 | -9 | -15 | -19 | -22 | -23
42 |  | 26 | 29 | 32 | 35 | 38 | 41 | 42 | 43 | 44 | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 54 | 11 | 42 |  | 11 | 11 | 8 | 5 | 6 | 5 | 5 | 3 | -1 | -4 | -7 | -7 | -8 | -14 | -18 | -21 | -22
43 |  | 27 | 30 | 33 | 36 | 39 | 42 | 43 | 44 | 45 | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 62 | 12 | 43 |  | 12 | 12 | 9 | 6 | 7 | 6 | 6 | 4 | 0 | -3 | -6 | -6 | -7 | -13 | -17 | -20 | -21
44 |  | 28 | 31 | 34 | 37 | 40 | 43 | 44 | 45 | 46 | 47 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 71 | 13 | 44 |  | 13 | 13 | 10 | 7 | 8 | 7 | 7 | 5 | 1 | -2 | -5 | -5 | -6 | -12 | -16 | -19 | -20
45 |  | 29 | 32 | 35 | 38 | 41 | 44 | 45 | 46 | 47 | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 80 | 14 | 45 |  | 14 | 14 | 11 | 8 | 9 | 8 | 8 | 6 | 2 | -1 | -4 | -4 | -5 | -11 | -15 | -18 | -19
46 |  | 30 | 33 | 36 | 39 | 42 | 45 | 46 | 47 | 48 | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 89 | 15 | 46 |  | 15 | 15 | 12 | 9 | 10 | 9 | 9 | 7 | 3 | 0 | -3 | -3 | -4 | -10 | -14 | -17 | -18
47 |  | 31 | 34 | 37 | 40 | 43 | 46 | 47 | 48 | 49 | 50 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 99 | 16 | 47 |  | 16 | 16 | 13 | 10 | 11 | 10 | 10 | 8 | 4 | 1 | -2 | -2 | -3 | -9 | -13 | -16 | -17
48 |  | 32 | 35 | 38 | 41 | 44 | 47 | 48 | 49 | 50 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 109 | 17 | 48 |  | 17 | 17 | 14 | 11 | 12 | 11 | 11 | 9 | 5 | 2 | -1 | -1 | -2 | -8 | -12 | -15 | -16
49 |  | 33 | 36 | 39 | 42 | 45 | 48 | 49 | 50 | 51 | 52 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 119 | 18 | 49 |  | 18 | 18 | 15 | 12 | 13 | 12 | 12 | 10 | 6 | 3 | 0 | 0 | -1 | -7 | -11 | -14 | -15
50 |  | 34 | 37 | 40 | 43 | 46 | 49 | 50 | 51 | 52 | 53 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 131 | 19 | 50 |  | 19 | 19 | 16 | 13 | 14 | 13 | 13 | 11 | 7 | 4 | 1 | 1 | 0 | -6 | -10 | -13 | -14
51 |  | 35 | 38 | 41 | 44 | 47 | 50 | 51 | 52 | 53 | 54 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 144 | 20 | 51 |  | 20 | 20 | 17 | 14 | 15 | 14 | 14 | 12 | 8 | 5 | 2 | 2 | 1 | -5 | -9 | -12 | -13
52 |  | 36 | 39 | 42 | 45 | 48 | 51 | 52 | 53 | 54 | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 157 | 21 | 52 |  | 21 | 21 | 18 | 15 | 16 | 15 | 15 | 13 | 9 | 6 | 3 | 3 | 2 | -4 | -8 | -11 | -12
53 |  | 37 | 40 | 43 | 46 | 49 | 52 | 53 | 54 | 55 | 56 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 170 | 22 | 53 |  | 22 | 22 | 19 | 16 | 17 | 16 | 16 | 14 | 10 | 7 | 4 | 4 | 3 | -3 | -7 | -10 | -11
54 |  | 38 | 41 | 44 | 47 | 50 | 53 | 54 | 55 | 56 | 57 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 183 | 23 | 54 |  | 23 | 23 | 20 | 17 | 18 | 17 | 17 | 15 | 11 | 8 | 5 | 5 | 4 | -2 | -6 | -9 | -10
55 |  | 39 | 42 | 45 | 48 | 51 | 54 | 55 | 56 | 57 | 58 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 196 | 24 | 55 |  | 24 | 24 | 21 | 18 | 19 | 18 | 18 | 16 | 12 | 9 | 6 | 6 | 5 | -1 | -5 | -8 | -9
56 |  | 40 | 43 | 46 | 49 | 52 | 55 | 56 | 57 | 58 | 59 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 209 | 25 | 56 |  | 25 | 25 | 22 | 19 | 20 | 19 | 19 | 17 | 13 | 10 | 7 | 7 | 6 | 0 | -4 | -7 | -8
57 |  | 41 | 44 | 47 | 50 | 53 | 56 | 57 | 58 | 59 | 60 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 223 | 26 | 57 |  | 26 | 26 | 23 | 20 | 21 | 20 | 20 | 18 | 14 | 11 | 8 | 8 | 7 | 1 | -3 | -6 | -7
58 |  | 42 | 45 | 48 | 51 | 54 | 57 | 58 | 59 | 60 | 61 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 237 | 27 | 58 |  | 27 | 27 | 24 | 21 | 22 | 21 | 21 | 19 | 15 | 12 | 9 | 9 | 8 | 2 | -2 | -5 | -6
59 |  | 43 | 46 | 49 | 52 | 55 | 58 | 59 | 60 | 61 | 62 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 251 | 28 | 59 |  | 28 | 28 | 25 | 22 | 23 | 22 | 22 | 20 | 16 | 13 | 10 | 10 | 9 | 3 | -1 | -4 | -5
60 |  | 44 | 47 | 50 | 53 | 56 | 59 | 60 | 61 | 62 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 265 | 29 | 60 |  | 29 | 29 | 26 | 23 | 24 | 23 | 23 | 21 | 17 | 14 | 11 | 11 | 10 | 4 | 0 | -3 | -4
61 |  | 45 | 48 | 51 | 54 | 57 | 60 | 61 | 62 | 63 | 64 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 280 | 30 | 61 |  | 30 | 30 | 27 | 24 | 25 | 24 | 24 | 22 | 18 | 15 | 12 | 12 | 11 | 5 | 1 | -2 | -3
62 |  | 46 | 49 | 52 | 55 | 58 | 61 | 62 | 63 | 64 | 65 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 295 | 31 | 62 |  | 31 | 31 | 28 | 25 | 26 | 25 | 25 | 23 | 19 | 16 | 13 | 13 | 12 | 6 | 2 | -1 | -2
63 |  | 47 | 50 | 53 | 56 | 59 | 62 | 63 | 64 | 65 | 66 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 310 | 32 | 63 |  | 32 | 32 | 29 | 26 | 27 | 26 | 26 | 24 | 20 | 17 | 14 | 14 | 13 | 7 | 3 | 0 | -1
64 |  | 48 | 51 | 54 | 57 | 60 | 63 | 64 | 65 | 66 | 67 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 326 | 33 | 64 |  | 33 | 33 | 30 | 27 | 28 | 27 | 27 | 25 | 21 | 18 | 15 | 15 | 14 | 8 | 4 | 1 | 0
65 |  | 49 | 52 | 55 | 58 | 61 | 64 | 65 | 66 | 67 | 68 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 342 | 34 | 65 |  | 34 | 34 | 31 | 28 | 29 | 28 | 28 | 26 | 22 | 19 | 16 | 16 | 15 | 9 | 5 | 2 | 1
66 |  | 50 | 53 | 56 | 59 | 62 | 65 | 66 | 67 | 68 | 69 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 358 | 35 | 66 |  | 35 | 35 | 32 | 29 | 30 | 29 | 29 | 27 | 23 | 20 | 17 | 17 | 16 | 10 | 6 | 3 | 2
67 |  | 51 | 54 | 57 | 60 | 63 | 66 | 67 | 68 | 69 | 70 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 374 | 36 | 67 |  | 36 | 36 | 33 | 30 | 31 | 30 | 30 | 28 | 24 | 21 | 18 | 18 | 17 | 11 | 7 | 4 | 3
68 |  | 52 | 55 | 58 | 61 | 64 | 67 | 68 | 69 | 70 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 390 | 37 | 68 |  | 37 | 37 | 34 | 31 | 32 | 31 | 31 | 29 | 25 | 22 | 19 | 19 | 18 | 12 | 8 | 5 | 4
69 |  | 53 | 56 | 59 | 62 | 65 | 68 | 69 | 70 | 71 | 72 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 406 | 38 | 69 |  | 38 | 38 | 35 | 32 | 33 | 32 | 32 | 30 | 26 | 23 | 20 | 20 | 19 | 13 | 9 | 6 | 5
70 |  | 54 | 57 | 60 | 63 | 66 | 69 | 70 | 71 | 72 | 73 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 422 | 39 | 70 |  | 39 | 39 | 36 | 33 | 34 | 33 | 33 | 31 | 27 | 24 | 21 | 21 | 20 | 14 | 10 | 7 | 6
71 |  | 55 | 58 | 61 | 64 | 67 | 70 | 71 | 72 | 73 | 74 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 438 | 40 | 71 |  | 40 | 40 | 37 | 34 | 35 | 34 | 34 | 32 | 28 | 25 | 22 | 22 | 21 | 15 | 11 | 8 | 7
72 |  | 56 | 59 | 62 | 65 | 68 | 71 | 72 | 73 | 74 | 75 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 454 | 41 | 72 |  | 41 | 41 | 38 | 35 | 36 | 35 | 35 | 33 | 29 | 26 | 23 | 23 | 22 | 16 | 12 | 9 | 8
73 |  | 57 | 60 | 63 | 66 | 69 | 72 | 73 | 74 | 75 | 76 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 470 | 42 | 73 |  | 42 | 42 | 39 | 36 | 37 | 36 | 36 | 34 | 30 | 27 | 24 | 24 | 23 | 17 | 13 | 10 | 9
74 |  | 58 | 61 | 64 | 67 | 70 | 73 | 74 | 75 | 76 | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 486 | 43 | 74 |  | 43 | 43 | 40 | 37 | 38 | 37 | 37 | 35 | 31 | 28 | 25 | 25 | 24 | 18 | 14 | 11 | 10
75 |  | 59 | 62 | 65 | 68 | 71 | 74 | 75 | 76 | 77 | 78 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 502 | 44 | 75 |  | 44 | 44 | 41 | 38 | 39 | 38 | 38 | 36 | 32 | 29 | 26 | 26 | 25 | 19 | 15 | 12 | 11
76 |  | 60 | 63 | 66 | 69 | 72 | 75 | 76 | 77 | 78 | 79 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 518 | 45 | 76 |  | 45 | 45 | 42 | 39 | 40 | 39 | 39 | 37 | 33 | 30 | 27 | 27 | 26 | 20 | 16 | 13 | 12
77 |  | 61 | 64 | 67 | 70 | 73 | 76 | 77 | 78 | 79 | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 534 | 46 | 77 |  | 46 | 46 | 43 | 40 | 41 | 40 | 40 | 38 | 34 | 31 | 28 | 28 | 27 | 21 | 17 | 14 | 13
78 |  | 62 | 65 | 68 | 71 | 74 | 77 | 78 | 79 | 80 | 81 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 550 | 47 | 78 |  | 47 | 47 | 44 | 41 | 42 | 41 | 41 | 39 | 35 | 32 | 29 | 29 | 28 | 22 | 18 | 15 | 14
79 |  | 63 | 66 | 69 | 72 | 75 | 78 | 79 | 80 | 81 | 82 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 566 | 48 | 79 |  | 48 | 48 | 45 | 42 | 43 | 42 | 42 | 40 | 36 | 33 | 30 | 30 | 29 | 23 | 19 | 16 | 15
80 |  | 64 | 67 | 70 | 73 | 76 | 79 | 80 | 81 | 82 | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 582 | 49 | 80 |  | 49 | 49 | 46 | 43 | 44 | 43 | 43 | 41 | 37 | 34 | 31 | 31 | 30 | 24 | 20 | 17 | 16
81 |  | 65 | 68 | 71 | 74 | 77 | 80 | 81 | 82 | 83 | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 598 | 50 | 81 |  | 50 | 50 | 47 | 44 | 45 | 44 | 44 | 42 | 38 | 35 | 32 | 32 | 31 | 25 | 21 | 18 | 17
82 |  | 66 | 69 | 72 | 75 | 78 | 81 | 82 | 83 | 84 | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 614 | 51 | 82 |  | 51 | 51 | 48 | 45 | 46 | 45 | 45 | 43 | 39 | 36 | 33 | 33 | 32 | 26 | 22 | 19 | 18
83 |  | 67 | 70 | 73 | 76 | 79 | 82 | 83 | 84 | 85 | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 630 | 52 | 83 |  | 52 | 52 | 49 | 46 | 47 | 46 | 46 | 44 | 40 | 37 | 34 | 34 | 33 | 27 | 23 | 20 | 19
84 |  | 68 | 71 | 74 | 77 | 80 | 83 | 84 | 85 | 86 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 646 | 53 | 84 |  | 53 | 53 | 50 | 47 | 48 | 47 | 47 | 45 | 41 | 38 | 35 | 35 | 34 | 28 | 24 | 21 | 20
85 |  | 69 | 72 | 75 | 78 | 81 | 84 | 85 | 86 | 87 | 88 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 662 | 54 | 85 |  | 54 | 54 | 51 | 48 | 49 | 48 | 48 | 46 | 42 | 39 | 36 | 36 | 35 | 29 | 25 | 22 | 21
86 |  | 70 | 73 | 76 | 79 | 82 | 85 | 86 | 87 | 88 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 678 | 55 | 86 |  | 55 | 55 | 52 | 49 | 50 | 49 | 49 | 47 | 43 | 40 | 37 | 37 | 36 | 30 | 26 | 23 | 22
87 |  | 71 | 74 | 77 | 80 | 83 | 86 | 87 | 88 | 89 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 694 | 56 | 87 |  | 56 | 56 | 53 | 50 | 51 | 50 | 50 | 48 | 44 | 41 | 38 | 38 | 37 | 31 | 27 | 24 | 23
88 |  | 72 | 75 | 78 | 81 | 84 | 87 | 88 | 89 | 90 | 91 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 710 | 57 | 88 |  | 57 | 57 | 54 | 51 | 52 | 51 | 51 | 49 | 45 | 42 | 39 | 39 | 38 | 32 | 28 | 25 | 24
89 |  | 73 | 76 | 79 | 82 | 85 | 88 | 89 | 90 | 91 | 92 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 726 | 58 | 89 |  | 58 | 58 | 55 | 52 | 53 | 52 | 52 | 50 | 46 | 43 | 40 | 40 | 39 | 33 | 29 | 26 | 25
90 |  | 74 | 77 | 80 | 83 | 86 | 89 | 90 | 91 | 92 | 93 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 742 | 59 | 90 |  | 59 | 59 | 56 | 53 | 54 | 53 | 53 | 51 | 47 | 44 | 41 | 41 | 40 | 34 | 30 | 27 | 26
91 |  | 75 | 78 | 81 | 84 | 87 | 90 | 91 | 92 | 93 | 94 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 758 | 60 | 91 |  | 60 | 60 | 57 | 54 | 55 | 54 | 54 | 52 | 48 | 45 | 42 | 42 | 41 | 35 | 31 | 28 | 27
92 |  | 76 | 79 | 82 | 85 | 88 | 91 | 92 | 93 | 94 | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 774 | 61 | 92 |  | 61 | 61 | 58 | 55 | 56 | 55 | 55 | 53 | 49 | 46 | 43 | 43 | 42 | 36 | 32 | 29 | 28
93 |  | 77 | 80 | 83 | 86 | 89 | 92 | 93 | 94 | 95 | 96 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 790 | 62 | 93 |  | 62 | 62 | 59 | 56 | 57 | 56 | 56 | 54 | 50 | 47 | 44 | 44 | 43 | 37 | 33 | 30 | 29
94 |  | 78 | 81 | 84 | 87 | 90 | 93 | 94 | 95 | 96 | 97 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 806 | 63 | 94 |  | 63 | 63 | 60 | 57 | 58 | 57 | 57 | 55 | 51 | 48 | 45 | 45 | 44 | 38 | 34 | 31 | 30
95 |  | 79 | 82 | 85 | 88 | 91 | 94 | 95 | 96 | 97 | 98 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 822 | 64 | 95 |  | 64 | 64 | 61 | 58 | 59 | 58 | 58 | 56 | 52 | 49 | 46 | 46 | 45 | 39 | 35 | 32 | 31
96 |  | 80 | 83 | 86 | 89 | 92 | 95 | 96 | 97 | 98 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 838 | 65 | 96 |  | 65 | 65 | 62 | 59 | 60 | 59 | 59 | 57 | 53 | 50 | 47 | 47 | 46 | 40 | 36 | 33 | 32
97 |  | 81 | 84 | 87 | 90 | 93 | 96 | 97 | 98 | 99 | 100 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 854 | 66 | 97 |  | 66 | 66 | 63 | 60 | 61 | 60 | 60 | 58 | 54 | 51 | 48 | 48 | 47 | 41 | 37 | 34 | 33
98 |  | 82 | 85 | 88 | 91 | 94 | 97 | 98 | 99 | 100 | 101 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 870 | 67 | 98 |  | 67 | 67 | 64 | 61 | 62 | 61 | 61 | 59 | 55 | 52 | 49 | 49 | 48 | 42 | 38 | 35 | 34
99 |  | 83 | 86 | 89 | 92 | 95 | 98 | 99 | 100 | 101 | 102 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 886 | 68 | 99 |  | 68 | 68 | 65 | 62 | 63 | 62 | 62 | 60 | 56 | 53 | 50 | 50 | 49 | 43 | 39 | 36 | 35
100 |  | 84 | 87 | 90 | 93 | 96 | 99 | 100 | 101 | 102 | 103 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 902 | 69 | 100 |  | 69 | 69 | 66 | 63 | 64 | 63 | 63 | 61 | 57 | 54 | 51 | 51 | 50 | 44 | 40 | 37 | 36
ANISPL | 82 | 83 | 79 | 76 | 77 | 74 | 69 | 63 | 56 | 50 | 46 | 47 | 45 | 45 | 41 | 38 | 34 | 31 | 23 | 26 | 38
IIC Contour | [18 empty] | Sum | max def | IIC Deficiencies
Contour | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 |  |  | Contour | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000
16 | 96 | 96 | 96 | 96 | 96 | 96 | 95 | 94 | 93 | 92 | 91 | 88 | 85 | 82 | 79 | 76 |  |  | 0 | -17 | 16 | -14 | -13 | -17 | -20 | -19 | -22 | -26 | -31 | -37 | -42 | -45 | -41 | -40 | -37 | -38 | -38
17 | 95 | 95 | 95 | 95 | 95 | 95 | 94 | 93 | 92 | 91 | 90 | 87 | 84 | 81 | 78 | 75 |  |  | 0 | -16 | 17 | -13 | -12 | -16 | -19 | -18 | -21 | -25 | -30 | -36 | -41 | -44 | -40 | -39 | -36 | -37 | -37
18 | 94 | 94 | 94 | 94 | 94 | 94 | 93 | 92 | 91 | 90 | 89 | 86 | 83 | 80 | 77 | 74 |  |  | 0 | -15 | 18 | -12 | -11 | -15 | -18 | -17 | -20 | -24 | -29 | -35 | -40 | -43 | -39 | -38 | -35 | -36 | -36
19 | 93 | 93 | 93 | 93 | 93 | 93 | 92 | 91 | 90 | 89 | 88 | 85 | 82 | 79 | 76 | 73 |  |  | 0 | -14 | 19 | -11 | -10 | -14 | -17 | -16 | -19 | -23 | -28 | -34 | -39 | -42 | -38 | -37 | -34 | -35 | -35
20 | 92 | 92 | 92 | 92 | 92 | 92 | 91 | 90 | 89 | 88 | 87 | 84 | 81 | 78 | 75 | 72 |  |  | 0 | -13 | 20 | -10 | -9 | -13 | -16 | -15 | -18 | -22 | -27 | -33 | -38 | -41 | -37 | -36 | -33 | -34 | -34
21 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 89 | 88 | 87 | 86 | 83 | 80 | 77 | 74 | 71 |  |  | 0 | -12 | 21 | -9 | -8 | -12 | -15 | -14 | -17 | -21 | -26 | -32 | -37 | -40 | -36 | -35 | -32 | -33 | -33
22 | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 88 | 87 | 86 | 85 | 82 | 79 | 76 | 73 | 70 |  |  | 0 | -11 | 22 | -8 | -7 | -11 | -14 | -13 | -16 | -20 | -25 | -31 | -36 | -39 | -35 | -34 | -31 | -32 | -32
23 | 89 | 89 | 89 | 89 | 89 | 89 | 88 | 87 | 86 | 85 | 84 | 81 | 78 | 75 | 72 | 69 |  |  | 0 | -10 | 23 | -7 | -6 | -10 | -13 | -12 | -15 | -19 | -24 | -30 | -35 | -38 | -34 | -33 | -30 | -31 | -31
24 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 86 | 85 | 84 | 83 | 80 | 77 | 74 | 71 | 68 |  |  | 0 | -9 | 24 | -6 | -5 | -9 | -12 | -11 | -14 | -18 | -23 | -29 | -34 | -37 | -33 | -32 | -29 | -30 | -30
25 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 85 | 84 | 83 | 82 | 79 | 76 | 73 | 70 | 67 |  |  | 0 | -8 | 25 | -5 | -4 | -8 | -11 | -10 | -13 | -17 | -22 | -28 | -33 | -36 | -32 | -31 | -28 | -29 | -29
26 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 84 | 83 | 82 | 81 | 78 | 75 | 72 | 69 | 66 |  |  | 0 | -7 | 26 | -4 | -3 | -7 | -10 | -9 | -12 | -16 | -21 | -27 | -32 | -35 | -31 | -30 | -27 | -28 | -28
27 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 83 | 82 | 81 | 80 | 77 | 74 | 71 | 68 | 65 |  |  | 0 | -6 | 27 | -3 | -2 | -6 | -9 | -8 | -11 | -15 | -20 | -26 | -31 | -34 | -30 | -29 | -26 | -27 | -27
28 | 84 | 84 | 84 | 84 | 84 | 84 | 83 | 82 | 81 | 80 | 79 | 76 | 73 | 70 | 67 | 64 |  |  | 0 | -5 | 28 | -2 | -1 | -5 | -8 | -7 | -10 | -14 | -19 | -25 | -30 | -33 | -29 | -28 | -25 | -26 | -26
29 | 83 | 83 | 83 | 83 | 83 | 83 | 82 | 81 | 80 | 79 | 78 | 75 | 72 | 69 | 66 | 63 |  |  | 0 | -4 | 29 | -1 | 0 | -4 | -7 | -6 | -9 | -13 | -18 | -24 | -29 | -32 | -28 | -27 | -24 | -25 | -25
30 | 82 | 82 | 82 | 82 | 82 | 82 | 81 | 80 | 79 | 78 | 77 | 74 | 71 | 68 | 65 | 62 |  |  | 1 | -3 | 30 | 0 | 1 | -3 | -6 | -5 | -8 | -12 | -17 | -23 | -28 | -31 | -27 | -26 | -23 | -24 | -24
31 | 81 | 81 | 81 | 81 | 81 | 81 | 80 | 79 | 78 | 77 | 76 | 73 | 70 | 67 | 64 | 61 |  |  | 3 | -2 | 31 | 1 | 2 | -2 | -5 | -4 | -7 | -11 | -16 | -22 | -27 | -30 | -26 | -25 | -22 | -23 | -23
32 | 80 | 80 | 80 | 80 | 80 | 80 | 79 | 78 | 77 | 76 | 75 | 72 | 69 | 66 | 63 | 60 |  |  | 5 | -1 | 32 | 2 | 3 | -1 | -4 | -3 | -6 | -10 | -15 | -21 | -26 | -29 | -25 | -24 | -21 | -22 | -22
33 | 79 | 79 | 79 | 79 | 79 | 79 | 78 | 77 | 76 | 75 | 74 | 71 | 68 | 65 | 62 | 59 |  |  | 7 | 0 | 33 | 3 | 4 | 0 | -3 | -2 | -5 | -9 | -14 | -20 | -25 | -28 | -24 | -23 | -20 | -21 | -21
34 | 78 | 78 | 78 | 78 | 78 | 78 | 77 | 76 | 75 | 74 | 73 | 70 | 67 | 64 | 61 | 58 |  |  | 10 | 1 | 34 | 4 | 5 | 1 | -2 | -1 | -4 | -8 | -13 | -19 | -24 | -27 | -23 | -22 | -19 | -20 | -20
35 | 77 | 77 | 77 | 77 | 77 | 77 | 76 | 75 | 74 | 73 | 72 | 69 | 66 | 63 | 60 | 57 |  |  | 13 | 2 | 35 | 5 | 6 | 2 | -1 | 0 | -3 | -7 | -12 | -18 | -23 | -26 | -22 | -21 | -18 | -19 | -19
36 | 76 | 76 | 76 | 76 | 76 | 76 | 75 | 74 | 73 | 72 | 71 | 68 | 65 | 62 | 59 | 56 |  |  | 17 | 3 | 36 | 6 | 7 | 3 | 0 | 1 | -2 | -6 | -11 | -17 | -22 | -25 | -21 | -20 | -17 | -18 | -18
37 | 75 | 75 | 75 | 75 | 75 | 75 | 74 | 73 | 72 | 71 | 70 | 67 | 64 | 61 | 58 | 55 |  |  | 22 | 4 | 37 | 7 | 8 | 4 | 1 | 2 | -1 | -5 | -10 | -16 | -21 | -24 | -20 | -19 | -16 | -17 | -17
38 | 74 | 74 | 74 | 74 | 74 | 74 | 73 | 72 | 71 | 70 | 69 | 66 | 63 | 60 | 57 | 54 |  |  | 27 | 5 | 38 | 8 | 9 | 5 | 2 | 3 | 0 | -4 | -9 | -15 | -20 | -23 | -19 | -18 | -15 | -16 | -16
39 | 73 | 73 | 73 | 73 | 73 | 73 | 72 | 71 | 70 | 69 | 68 | 65 | 62 | 59 | 56 | 53 |  |  | 33 | 6 | 39 | 9 | 10 | 6 | 3 | 4 | 1 | -3 | -8 | -14 | -19 | -22 | -18 | -17 | -14 | -15 | -15
40 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 70 | 69 | 68 | 67 | 64 | 61 | 58 | 55 | 52 |  |  | 39 | 7 | 40 | 10 | 11 | 7 | 4 | 5 | 2 | -2 | -7 | -13 | -18 | -21 | -17 | -16 | -13 | -14 | -14
41 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 69 | 68 | 67 | 66 | 63 | 60 | 57 | 54 | 51 |  |  | 45 | 8 | 41 | 11 | 12 | 8 | 5 | 6 | 3 | -1 | -6 | -12 | -17 | -20 | -16 | -15 | -12 | -13 | -13
42 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 68 | 67 | 66 | 65 | 62 | 59 | 56 | 53 | 50 |  |  | 51 | 9 | 42 | 12 | 13 | 9 | 6 | 7 | 4 | 0 | -5 | -11 | -16 | -19 | -15 | -14 | -11 | -12 | -12
43 | 69 | 69 | 69 | 69 | 69 | 69 | 68 | 67 | 66 | 65 | 64 | 61 | 58 | 55 | 52 | 49 |  |  | 58 | 10 | 43 | 13 | 14 | 10 | 7 | 8 | 5 | 1 | -4 | -10 | -15 | -18 | -14 | -13 | -10 | -11 | -11
44 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 66 | 65 | 64 | 63 | 60 | 57 | 54 | 51 | 48 |  |  | 65 | 11 | 44 | 14 | 15 | 11 | 8 | 9 | 6 | 2 | -3 | -9 | -14 | -17 | -13 | -12 | -9 | -10 | -10
45 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 65 | 64 | 63 | 62 | 59 | 56 | 53 | 50 | 47 |  |  | 72 | 12 | 45 | 15 | 16 | 12 | 9 | 10 | 7 | 3 | -2 | -8 | -13 | -16 | -12 | -11 | -8 | -9 | -9
46 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 64 | 63 | 62 | 61 | 58 | 55 | 52 | 49 | 46 |  |  | 79 | 13 | 46 | 16 | 17 | 13 | 10 | 11 | 8 | 4 | -1 | -7 | -12 | -15 | -11 | -10 | -7 | -8 | -8
47 | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 63 | 62 | 61 | 60 | 57 | 54 | 51 | 48 | 45 |  |  | 86 | 14 | 47 | 17 | 18 | 14 | 11 | 12 | 9 | 5 | 0 | -6 | -11 | -14 | -10 | -9 | -6 | -7 | -7
48 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 62 | 61 | 60 | 59 | 56 | 53 | 50 | 47 | 44 |  |  | 94 | 15 | 48 | 18 | 19 | 15 | 12 | 13 | 10 | 6 | 1 | -5 | -10 | -13 | -9 | -8 | -5 | -6 | -6
49 | 63 | 63 | 63 | 63 | 63 | 63 | 62 | 61 | 60 | 59 | 58 | 55 | 52 | 49 | 46 | 43 |  |  | 102 | 16 | 49 | 19 | 20 | 16 | 13 | 14 | 11 | 7 | 2 | -4 | -9 | -12 | -8 | -7 | -4 | -5 | -5
50 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 60 | 59 | 58 | 57 | 54 | 51 | 48 | 45 | 42 |  |  | 110 | 17 | 50 | 20 | 21 | 17 | 14 | 15 | 12 | 8 | 3 | -3 | -8 | -11 | -7 | -6 | -3 | -4 | -4
51 | 61 | 61 | 61 | 61 | 61 | 61 | 60 | 59 | 58 | 57 | 56 | 53 | 50 | 47 | 44 | 41 |  |  | 118 | 18 | 51 | 21 | 22 | 18 | 15 | 16 | 13 | 9 | 4 | -2 | -7 | -10 | -6 | -5 | -2 | -3 | -3
52 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 58 | 57 | 56 | 55 | 52 | 49 | 46 | 43 | 40 |  |  | 126 | 19 | 52 | 22 | 23 | 19 | 16 | 17 | 14 | 10 | 5 | -1 | -6 | -9 | -5 | -4 | -1 | -2 | -2
53 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 57 | 56 | 55 | 54 | 51 | 48 | 45 | 42 | 39 |  |  | 134 | 20 | 53 | 23 | 24 | 20 | 17 | 18 | 15 | 11 | 6 | 0 | -5 | -8 | -4 | -3 | 0 | -1 | -1
54 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 56 | 55 | 54 | 53 | 50 | 47 | 44 | 41 | 38 |  |  | 144 | 21 | 54 | 24 | 25 | 21 | 18 | 19 | 16 | 12 | 7 | 1 | -4 | -7 | -3 | -2 | 1 | 0 | 0
55 | 57 | 57 | 57 | 57 | 57 | 57 | 56 | 55 | 54 | 53 | 52 | 49 | 46 | 43 | 40 | 37 |  |  | 156 | 22 | 55 | 25 | 26 | 22 | 19 | 20 | 17 | 13 | 8 | 2 | -3 | -6 | -2 | -1 | 2 | 1 | 1
56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 54 | 53 | 52 | 51 | 48 | 45 | 42 | 39 | 36 |  |  | 168 | 23 | 56 | 26 | 27 | 23 | 20 | 21 | 18 | 14 | 9 | 3 | -2 | -5 | -1 | 0 | 3 | 2 | 2
57 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 53 | 52 | 51 | 50 | 47 | 44 | 41 | 38 | 35 |  |  | 181 | 24 | 57 | 27 | 28 | 24 | 21 | 22 | 19 | 15 | 10 | 4 | -1 | -4 | 0 | 1 | 4 | 3 | 3
58 | 54 | 54 | 54 | 54 | 54 | 54 | 53 | 52 | 51 | 50 | 49 | 46 | 43 | 40 | 37 | 34 |  |  | 195 | 25 | 58 | 28 | 29 | 25 | 22 | 23 | 20 | 16 | 11 | 5 | 0 | -3 | 1 | 2 | 5 | 4 | 4
59 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 51 | 50 | 49 | 48 | 45 | 42 | 39 | 36 | 33 |  |  | 210 | 26 | 59 | 29 | 30 | 26 | 23 | 24 | 21 | 17 | 12 | 6 | 1 | -2 | 2 | 3 | 6 | 5 | 5
60 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 50 | 49 | 48 | 47 | 44 | 41 | 38 | 35 | 32 |  |  | 225 | 27 | 60 | 30 | 31 | 27 | 24 | 25 | 22 | 18 | 13 | 7 | 2 | -1 | 3 | 4 | 7 | 6 | 6
61 | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 49 | 48 | 47 | 46 | 43 | 40 | 37 | 34 | 31 |  |  | 240 | 28 | 61 | 31 | 32 | 28 | 25 | 26 | 23 | 19 | 14 | 8 | 3 | 0 | 4 | 5 | 8 | 7 | 7
62 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 48 | 47 | 46 | 45 | 42 | 39 | 36 | 33 | 30 |  |  | 256 | 29 | 62 | 32 | 33 | 29 | 26 | 27 | 24 | 20 | 15 | 9 | 4 | 1 | 5 | 6 | 9 | 8 | 8
63 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 47 | 46 | 45 | 44 | 41 | 38 | 35 | 32 | 29 |  |  | 272 | 30 | 63 | 33 | 34 | 30 | 27 | 28 | 25 | 21 | 16 | 10 | 5 | 2 | 6 | 7 | 10 | 9 | 9
64 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 46 | 45 | 44 | 43 | 40 | 37 | 34 | 31 | 28 |  |  | 288 | 31 | 64 | 34 | 35 | 31 | 28 | 29 | 26 | 22 | 17 | 11 | 6 | 3 | 7 | 8 | 11 | 10 | 10
65 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 45 | 44 | 43 | 42 | 39 | 36 | 33 | 30 | 27 |  |  | 304 | 32 | 65 | 35 | 36 | 32 | 29 | 30 | 27 | 23 | 18 | 12 | 7 | 4 | 8 | 9 | 12 | 11 | 11
66 | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 44 | 43 | 42 | 41 | 38 | 35 | 32 | 29 | 26 |  |  | 320 | 33 | 66 | 36 | 37 | 33 | 30 | 31 | 28 | 24 | 19 | 13 | 8 | 5 | 9 | 10 | 13 | 12 | 12
67 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 43 | 42 | 41 | 40 | 37 | 34 | 31 | 28 | 25 |  |  | 336 | 34 | 67 | 37 | 38 | 34 | 31 | 32 | 29 | 25 | 20 | 14 | 9 | 6 | 10 | 11 | 14 | 13 | 13
68 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 42 | 41 | 40 | 39 | 36 | 33 | 30 | 27 | 24 |  |  | 352 | 35 | 68 | 38 | 39 | 35 | 32 | 33 | 30 | 26 | 21 | 15 | 10 | 7 | 11 | 12 | 15 | 14 | 14
69 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 41 | 40 | 39 | 38 | 35 | 32 | 29 | 26 | 23 |  |  | 368 | 36 | 69 | 39 | 40 | 36 | 33 | 34 | 31 | 27 | 22 | 16 | 11 | 8 | 12 | 13 | 16 | 15 | 15
70 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 40 | 39 | 38 | 37 | 34 | 31 | 28 | 25 | 22 |  |  | 384 | 37 | 70 | 40 | 41 | 37 | 34 | 35 | 32 | 28 | 23 | 17 | 12 | 9 | 13 | 14 | 17 | 16 | 16
71 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 39 | 38 | 37 | 36 | 33 | 30 | 27 | 24 | 21 |  |  | 400 | 38 | 71 | 41 | 42 | 38 | 35 | 36 | 33 | 29 | 24 | 18 | 13 | 10 | 14 | 15 | 18 | 17 | 17
72 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 38 | 37 | 36 | 35 | 32 | 29 | 26 | 23 | 20 |  |  | 416 | 39 | 72 | 42 | 43 | 39 | 36 | 37 | 34 | 30 | 25 | 19 | 14 | 11 | 15 | 16 | 19 | 18 | 18
73 | 39 | 39 | 39 | 39 | 39 | 39 | 38 | 37 | 36 | 35 | 34 | 31 | 28 | 25 | 22 | 19 |  |  | 432 | 40 | 73 | 43 | 44 | 40 | 37 | 38 | 35 | 31 | 26 | 20 | 15 | 12 | 16 | 17 | 20 | 19 | 19
74 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 36 | 35 | 34 | 33 | 30 | 27 | 24 | 21 | 18 |  |  | 448 | 41 | 74 | 44 | 45 | 41 | 38 | 39 | 36 | 32 | 27 | 21 | 16 | 13 | 17 | 18 | 21 | 20 | 20
75 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 35 | 34 | 33 | 32 | 29 | 26 | 23 | 20 | 17 |  |  | 464 | 42 | 75 | 45 | 46 | 42 | 39 | 40 | 37 | 33 | 28 | 22 | 17 | 14 | 18 | 19 | 22 | 21 | 21
76 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 34 | 33 | 32 | 31 | 28 | 25 | 22 | 19 | 16 |  |  | 480 | 43 | 76 | 46 | 47 | 43 | 40 | 41 | 38 | 34 | 29 | 23 | 18 | 15 | 19 | 20 | 23 | 22 | 22
77 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 33 | 32 | 31 | 30 | 27 | 24 | 21 | 18 | 15 |  |  | 496 | 44 | 77 | 47 | 48 | 44 | 41 | 42 | 39 | 35 | 30 | 24 | 19 | 16 | 20 | 21 | 24 | 23 | 23
78 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 32 | 31 | 30 | 29 | 26 | 23 | 20 | 17 | 14 |  |  | 512 | 45 | 78 | 48 | 49 | 45 | 42 | 43 | 40 | 36 | 31 | 25 | 20 | 17 | 21 | 22 | 25 | 24 | 24
79 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 31 | 30 | 29 | 28 | 25 | 22 | 19 | 16 | 13 |  |  | 528 | 46 | 79 | 49 | 50 | 46 | 43 | 44 | 41 | 37 | 32 | 26 | 21 | 18 | 22 | 23 | 26 | 25 | 25
80 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 30 | 29 | 28 | 27 | 24 | 21 | 18 | 15 | 12 |  |  | 544 | 47 | 80 | 50 | 51 | 47 | 44 | 45 | 42 | 38 | 33 | 27 | 22 | 19 | 23 | 24 | 27 | 26 | 26
81 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 29 | 28 | 27 | 26 | 23 | 20 | 17 | 14 | 11 |  |  | 560 | 48 | 81 | 51 | 52 | 48 | 45 | 46 | 43 | 39 | 34 | 28 | 23 | 20 | 24 | 25 | 28 | 27 | 27
82 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 28 | 27 | 26 | 25 | 22 | 19 | 16 | 13 | 10 |  |  | 576 | 49 | 82 | 52 | 53 | 49 | 46 | 47 | 44 | 40 | 35 | 29 | 24 | 21 | 25 | 26 | 29 | 28 | 28
83 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 27 | 26 | 25 | 24 | 21 | 18 | 15 | 12 | 9 |  |  | 592 | 50 | 83 | 53 | 54 | 50 | 47 | 48 | 45 | 41 | 36 | 30 | 25 | 22 | 26 | 27 | 30 | 29 | 29
84 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 26 | 25 | 24 | 23 | 20 | 17 | 14 | 11 | 8 |  |  | 608 | 51 | 84 | 54 | 55 | 51 | 48 | 49 | 46 | 42 | 37 | 31 | 26 | 23 | 27 | 28 | 31 | 30 | 30
85 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 25 | 24 | 23 | 22 | 19 | 16 | 13 | 10 | 7 |  |  | 624 | 52 | 85 | 55 | 56 | 52 | 49 | 50 | 47 | 43 | 38 | 32 | 27 | 24 | 28 | 29 | 32 | 31 | 31
86 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 24 | 23 | 22 | 21 | 18 | 15 | 12 | 9 | 6 |  |  | 640 | 53 | 86 | 56 | 57 | 53 | 50 | 51 | 48 | 44 | 39 | 33 | 28 | 25 | 29 | 30 | 33 | 32 | 32
87 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 23 | 22 | 21 | 20 | 17 | 14 | 11 | 8 | 5 |  |  | 656 | 54 | 87 | 57 | 58 | 54 | 51 | 52 | 49 | 45 | 40 | 34 | 29 | 26 | 30 | 31 | 34 | 33 | 33
88 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 22 | 21 | 20 | 19 | 16 | 13 | 10 | 7 | 4 |  |  | 672 | 55 | 88 | 58 | 59 | 55 | 52 | 53 | 50 | 46 | 41 | 35 | 30 | 27 | 31 | 32 | 35 | 34 | 34
89 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 21 | 20 | 19 | 18 | 15 | 12 | 9 | 6 | 3 |  |  | 688 | 56 | 89 | 59 | 60 | 56 | 53 | 54 | 51 | 47 | 42 | 36 | 31 | 28 | 32 | 33 | 36 | 35 | 35
90 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 19 | 18 | 17 | 14 | 11 | 8 | 5 | 2 |  |  | 704 | 57 | 90 | 60 | 61 | 57 | 54 | 55 | 52 | 48 | 43 | 37 | 32 | 29 | 33 | 34 | 37 | 36 | 36
91 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 19 | 18 | 17 | 16 | 13 | 10 | 7 | 4 | 1 |  |  | 720 | 58 | 91 | 61 | 62 | 58 | 55 | 56 | 53 | 49 | 44 | 38 | 33 | 30 | 34 | 35 | 38 | 37 | 37
92 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 18 | 17 | 16 | 15 | 12 | 9 | 6 | 3 | 0 |  |  | 736 | 59 | 92 | 62 | 63 | 59 | 56 | 57 | 54 | 50 | 45 | 39 | 34 | 31 | 35 | 36 | 39 | 38 | 38
93 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 17 | 16 | 15 | 14 | 11 | 8 | 5 | 2 | -1 |  |  | 752 | 60 | 93 | 63 | 64 | 60 | 57 | 58 | 55 | 51 | 46 | 40 | 35 | 32 | 36 | 37 | 40 | 39 | 39
94 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 16 | 15 | 14 | 13 | 10 | 7 | 4 | 1 | -2 |  |  | 768 | 61 | 94 | 64 | 65 | 61 | 58 | 59 | 56 | 52 | 47 | 41 | 36 | 33 | 37 | 38 | 41 | 40 | 40
95 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 15 | 14 | 13 | 12 | 9 | 6 | 3 | 0 | -3 |  |  | 784 | 62 | 95 | 65 | 66 | 62 | 59 | 60 | 57 | 53 | 48 | 42 | 37 | 34 | 38 | 39 | 42 | 41 | 41
96 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 14 | 13 | 12 | 11 | 8 | 5 | 2 | -1 | -4 |  |  | 800 | 63 | 96 | 66 | 67 | 63 | 60 | 61 | 58 | 54 | 49 | 43 | 38 | 35 | 39 | 40 | 43 | 42 | 42
97 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 13 | 12 | 11 | 10 | 7 | 4 | 1 | -2 | -5 |  |  | 816 | 64 | 97 | 67 | 68 | 64 | 61 | 62 | 59 | 55 | 50 | 44 | 39 | 36 | 40 | 41 | 44 | 43 | 43
98 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 12 | 11 | 10 | 9 | 6 | 3 | 0 | -3 | -6 |  |  | 832 | 65 | 98 | 68 | 69 | 65 | 62 | 63 | 60 | 56 | 51 | 45 | 40 | 37 | 41 | 42 | 45 | 44 | 44
99 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 11 | 10 | 9 | 8 | 5 | 2 | -1 | -4 | -7 |  |  | 848 | 66 | 99 | 69 | 70 | 66 | 63 | 64 | 61 | 57 | 52 | 46 | 41 | 38 | 42 | 43 | 46 | 45 | 45
100 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 10 | 9 | 8 | 7 | 4 | 1 | -2 | -5 | -8 |  |  | 864 | 67 | 100 | 70 | 71 | 67 | 64 | 65 | 62 | 58 | 53 | 47 | 42 | 39 | 43 | 44 | 47 | 46 | 46
ISPL | 77.134 | 79.2538 | 74.4402 | 73.2975 | 74.3392 | 71.611 | 67.6428 | 61.7255 | 54.3417 | 48.3812 | 44.3479 | 45.9783 | 43.8788 | 44.3888 | 39.6455 | 36.4536 | 32.5693 | 29.757 | 27 | 31 | 42
ISR Contour | [18 empty] | Sum | max def | IIC Deficiencies
Contour | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 |  |  | Contour | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000
16 | 96 | 96 | 96 | 96 | 96 | 96 | 95 | 94 | 93 | 92 | 91 | 88 | 85 | 82 | 79 | 76 |  |  | 0 | -22 | 16 | -19 | -17 | -22 | -23 | -22 | -24 | -27 | -32 | -39 | -44 | -47 | -42 | -41 | -38 | -39 | -40
17 | 95 | 95 | 95 | 95 | 95 | 95 | 94 | 93 | 92 | 91 | 90 | 87 | 84 | 81 | 78 | 75 |  |  | 0 | -21 | 17 | -18 | -16 | -21 | -22 | -21 | -23 | -26 | -31 | -38 | -43 | -46 | -41 | -40 | -37 | -38 | -39
18 | 94 | 94 | 94 | 94 | 94 | 94 | 93 | 92 | 91 | 90 | 89 | 86 | 83 | 80 | 77 | 74 |  |  | 0 | -20 | 18 | -17 | -15 | -20 | -21 | -20 | -22 | -25 | -30 | -37 | -42 | -45 | -40 | -39 | -36 | -37 | -38
19 | 93 | 93 | 93 | 93 | 93 | 93 | 92 | 91 | 90 | 89 | 88 | 85 | 82 | 79 | 76 | 73 |  |  | 0 | -19 | 19 | -16 | -14 | -19 | -20 | -19 | -21 | -24 | -29 | -36 | -41 | -44 | -39 | -38 | -35 | -36 | -37
20 | 92 | 92 | 92 | 92 | 92 | 92 | 91 | 90 | 89 | 88 | 87 | 84 | 81 | 78 | 75 | 72 |  |  | 0 | -18 | 20 | -15 | -13 | -18 | -19 | -18 | -20 | -23 | -28 | -35 | -40 | -43 | -38 | -37 | -34 | -35 | -36
21 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 89 | 88 | 87 | 86 | 83 | 80 | 77 | 74 | 71 |  |  | 0 | -17 | 21 | -14 | -12 | -17 | -18 | -17 | -19 | -22 | -27 | -34 | -39 | -42 | -37 | -36 | -33 | -34 | -35
22 | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 88 | 87 | 86 | 85 | 82 | 79 | 76 | 73 | 70 |  |  | 0 | -16 | 22 | -13 | -11 | -16 | -17 | -16 | -18 | -21 | -26 | -33 | -38 | -41 | -36 | -35 | -32 | -33 | -34
23 | 89 | 89 | 89 | 89 | 89 | 89 | 88 | 87 | 86 | 85 | 84 | 81 | 78 | 75 | 72 | 69 |  |  | 0 | -15 | 23 | -12 | -10 | -15 | -16 | -15 | -17 | -20 | -25 | -32 | -37 | -40 | -35 | -34 | -31 | -32 | -33
24 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 86 | 85 | 84 | 83 | 80 | 77 | 74 | 71 | 68 |  |  | 0 | -14 | 24 | -11 | -9 | -14 | -15 | -14 | -16 | -19 | -24 | -31 | -36 | -39 | -34 | -33 | -30 | -31 | -32
25 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 85 | 84 | 83 | 82 | 79 | 76 | 73 | 70 | 67 |  |  | 0 | -13 | 25 | -10 | -8 | -13 | -14 | -13 | -15 | -18 | -23 | -30 | -35 | -38 | -33 | -32 | -29 | -30 | -31
26 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 84 | 83 | 82 | 81 | 78 | 75 | 72 | 69 | 66 |  |  | 0 | -12 | 26 | -9 | -7 | -12 | -13 | -12 | -14 | -17 | -22 | -29 | -34 | -37 | -32 | -31 | -28 | -29 | -30
27 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 83 | 82 | 81 | 80 | 77 | 74 | 71 | 68 | 65 |  |  | 0 | -11 | 27 | -8 | -6 | -11 | -12 | -11 | -13 | -16 | -21 | -28 | -33 | -36 | -31 | -30 | -27 | -28 | -29
28 | 84 | 84 | 84 | 84 | 84 | 84 | 83 | 82 | 81 | 80 | 79 | 76 | 73 | 70 | 67 | 64 |  |  | 0 | -10 | 28 | -7 | -5 | -10 | -11 | -10 | -12 | -15 | -20 | -27 | -32 | -35 | -30 | -29 | -26 | -27 | -28
29 | 83 | 83 | 83 | 83 | 83 | 83 | 82 | 81 | 80 | 79 | 78 | 75 | 72 | 69 | 66 | 63 |  |  | 0 | -9 | 29 | -6 | -4 | -9 | -10 | -9 | -11 | -14 | -19 | -26 | -31 | -34 | -29 | -28 | -25 | -26 | -27
30 | 82 | 82 | 82 | 82 | 82 | 82 | 81 | 80 | 79 | 78 | 77 | 74 | 71 | 68 | 65 | 62 |  |  | 0 | -8 | 30 | -5 | -3 | -8 | -9 | -8 | -10 | -13 | -18 | -25 | -30 | -33 | -28 | -27 | -24 | -25 | -26
31 | 81 | 81 | 81 | 81 | 81 | 81 | 80 | 79 | 78 | 77 | 76 | 73 | 70 | 67 | 64 | 61 |  |  | 0 | -7 | 31 | -4 | -2 | -7 | -8 | -7 | -9 | -12 | -17 | -24 | -29 | -32 | -27 | -26 | -23 | -24 | -25
32 | 80 | 80 | 80 | 80 | 80 | 80 | 79 | 78 | 77 | 76 | 75 | 72 | 69 | 66 | 63 | 60 |  |  | 0 | -6 | 32 | -3 | -1 | -6 | -7 | -6 | -8 | -11 | -16 | -23 | -28 | -31 | -26 | -25 | -22 | -23 | -24
33 | 79 | 79 | 79 | 79 | 79 | 79 | 78 | 77 | 76 | 75 | 74 | 71 | 68 | 65 | 62 | 59 |  |  | 0 | -5 | 33 | -2 | 0 | -5 | -6 | -5 | -7 | -10 | -15 | -22 | -27 | -30 | -25 | -24 | -21 | -22 | -23
34 | 78 | 78 | 78 | 78 | 78 | 78 | 77 | 76 | 75 | 74 | 73 | 70 | 67 | 64 | 61 | 58 |  |  | 1 | -4 | 34 | -1 | 1 | -4 | -5 | -4 | -6 | -9 | -14 | -21 | -26 | -29 | -24 | -23 | -20 | -21 | -22
35 | 77 | 77 | 77 | 77 | 77 | 77 | 76 | 75 | 74 | 73 | 72 | 69 | 66 | 63 | 60 | 57 |  |  | 2 | -3 | 35 | 0 | 2 | -3 | -4 | -3 | -5 | -8 | -13 | -20 | -25 | -28 | -23 | -22 | -19 | -20 | -21
36 | 76 | 76 | 76 | 76 | 76 | 76 | 75 | 74 | 73 | 72 | 71 | 68 | 65 | 62 | 59 | 56 |  |  | 4 | -2 | 36 | 1 | 3 | -2 | -3 | -2 | -4 | -7 | -12 | -19 | -24 | -27 | -22 | -21 | -18 | -19 | -20
37 | 75 | 75 | 75 | 75 | 75 | 75 | 74 | 73 | 72 | 71 | 70 | 67 | 64 | 61 | 58 | 55 |  |  | 6 | -1 | 37 | 2 | 4 | -1 | -2 | -1 | -3 | -6 | -11 | -18 | -23 | -26 | -21 | -20 | -17 | -18 | -19
38 | 74 | 74 | 74 | 74 | 74 | 74 | 73 | 72 | 71 | 70 | 69 | 66 | 63 | 60 | 57 | 54 |  |  | 8 | 0 | 38 | 3 | 5 | 0 | -1 | 0 | -2 | -5 | -10 | -17 | -22 | -25 | -20 | -19 | -16 | -17 | -18
39 | 73 | 73 | 73 | 73 | 73 | 73 | 72 | 71 | 70 | 69 | 68 | 65 | 62 | 59 | 56 | 53 |  |  | 12 | 1 | 39 | 4 | 6 | 1 | 0 | 1 | -1 | -4 | -9 | -16 | -21 | -24 | -19 | -18 | -15 | -16 | -17
40 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 70 | 69 | 68 | 67 | 64 | 61 | 58 | 55 | 52 |  |  | 17 | 2 | 40 | 5 | 7 | 2 | 1 | 2 | 0 | -3 | -8 | -15 | -20 | -23 | -18 | -17 | -14 | -15 | -16
41 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 69 | 68 | 67 | 66 | 63 | 60 | 57 | 54 | 51 |  |  | 23 | 3 | 41 | 6 | 8 | 3 | 2 | 3 | 1 | -2 | -7 | -14 | -19 | -22 | -17 | -16 | -13 | -14 | -15
42 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 68 | 67 | 66 | 65 | 62 | 59 | 56 | 53 | 50 |  |  | 29 | 4 | 42 | 7 | 9 | 4 | 3 | 4 | 2 | -1 | -6 | -13 | -18 | -21 | -16 | -15 | -12 | -13 | -14
43 | 69 | 69 | 69 | 69 | 69 | 69 | 68 | 67 | 66 | 65 | 64 | 61 | 58 | 55 | 52 | 49 |  |  | 35 | 5 | 43 | 8 | 10 | 5 | 4 | 5 | 3 | 0 | -5 | -12 | -17 | -20 | -15 | -14 | -11 | -12 | -13
44 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 66 | 65 | 64 | 63 | 60 | 57 | 54 | 51 | 48 |  |  | 42 | 6 | 44 | 9 | 11 | 6 | 5 | 6 | 4 | 1 | -4 | -11 | -16 | -19 | -14 | -13 | -10 | -11 | -12
45 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 65 | 64 | 63 | 62 | 59 | 56 | 53 | 50 | 47 |  |  | 49 | 7 | 45 | 10 | 12 | 7 | 6 | 7 | 5 | 2 | -3 | -10 | -15 | -18 | -13 | -12 | -9 | -10 | -11
46 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 64 | 63 | 62 | 61 | 58 | 55 | 52 | 49 | 46 |  |  | 56 | 8 | 46 | 11 | 13 | 8 | 7 | 8 | 6 | 3 | -2 | -9 | -14 | -17 | -12 | -11 | -8 | -9 | -10
47 | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 63 | 62 | 61 | 60 | 57 | 54 | 51 | 48 | 45 |  |  | 63 | 9 | 47 | 12 | 14 | 9 | 8 | 9 | 7 | 4 | -1 | -8 | -13 | -16 | -11 | -10 | -7 | -8 | -9
48 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 62 | 61 | 60 | 59 | 56 | 53 | 50 | 47 | 44 |  |  | 70 | 10 | 48 | 13 | 15 | 10 | 9 | 10 | 8 | 5 | 0 | -7 | -12 | -15 | -10 | -9 | -6 | -7 | -8
49 | 63 | 63 | 63 | 63 | 63 | 63 | 62 | 61 | 60 | 59 | 58 | 55 | 52 | 49 | 46 | 43 |  |  | 78 | 11 | 49 | 14 | 16 | 11 | 10 | 11 | 9 | 6 | 1 | -6 | -11 | -14 | -9 | -8 | -5 | -6 | -7
50 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 60 | 59 | 58 | 57 | 54 | 51 | 48 | 45 | 42 |  |  | 86 | 12 | 50 | 15 | 17 | 12 | 11 | 12 | 10 | 7 | 2 | -5 | -10 | -13 | -8 | -7 | -4 | -5 | -6
51 | 61 | 61 | 61 | 61 | 61 | 61 | 60 | 59 | 58 | 57 | 56 | 53 | 50 | 47 | 44 | 41 |  |  | 94 | 13 | 51 | 16 | 18 | 13 | 12 | 13 | 11 | 8 | 3 | -4 | -9 | -12 | -7 | -6 | -3 | -4 | -5
52 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 58 | 57 | 56 | 55 | 52 | 49 | 46 | 43 | 40 |  |  | 102 | 14 | 52 | 17 | 19 | 14 | 13 | 14 | 12 | 9 | 4 | -3 | -8 | -11 | -6 | -5 | -2 | -3 | -4
53 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 57 | 56 | 55 | 54 | 51 | 48 | 45 | 42 | 39 |  |  | 110 | 15 | 53 | 18 | 20 | 15 | 14 | 15 | 13 | 10 | 5 | -2 | -7 | -10 | -5 | -4 | -1 | -2 | -3
54 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 56 | 55 | 54 | 53 | 50 | 47 | 44 | 41 | 38 |  |  | 118 | 16 | 54 | 19 | 21 | 16 | 15 | 16 | 14 | 11 | 6 | -1 | -6 | -9 | -4 | -3 | 0 | -1 | -2
55 | 57 | 57 | 57 | 57 | 57 | 57 | 56 | 55 | 54 | 53 | 52 | 49 | 46 | 43 | 40 | 37 |  |  | 127 | 17 | 55 | 20 | 22 | 17 | 16 | 17 | 15 | 12 | 7 | 0 | -5 | -8 | -3 | -2 | 1 | 0 | -1
56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 54 | 53 | 52 | 51 | 48 | 45 | 42 | 39 | 36 |  |  | 138 | 18 | 56 | 21 | 23 | 18 | 17 | 18 | 16 | 13 | 8 | 1 | -4 | -7 | -2 | -1 | 2 | 1 | 0
57 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 53 | 52 | 51 | 50 | 47 | 44 | 41 | 38 | 35 |  |  | 150 | 19 | 57 | 22 | 24 | 19 | 18 | 19 | 17 | 14 | 9 | 2 | -3 | -6 | -1 | 0 | 3 | 2 | 1
58 | 54 | 54 | 54 | 54 | 54 | 54 | 53 | 52 | 51 | 50 | 49 | 46 | 43 | 40 | 37 | 34 |  |  | 163 | 20 | 58 | 23 | 25 | 20 | 19 | 20 | 18 | 15 | 10 | 3 | -2 | -5 | 0 | 1 | 4 | 3 | 2
59 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 51 | 50 | 49 | 48 | 45 | 42 | 39 | 36 | 33 |  |  | 177 | 21 | 59 | 24 | 26 | 21 | 20 | 21 | 19 | 16 | 11 | 4 | -1 | -4 | 1 | 2 | 5 | 4 | 3
60 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 50 | 49 | 48 | 47 | 44 | 41 | 38 | 35 | 32 |  |  | 191 | 22 | 60 | 25 | 27 | 22 | 21 | 22 | 20 | 17 | 12 | 5 | 0 | -3 | 2 | 3 | 6 | 5 | 4
61 | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 49 | 48 | 47 | 46 | 43 | 40 | 37 | 34 | 31 |  |  | 206 | 23 | 61 | 26 | 28 | 23 | 22 | 23 | 21 | 18 | 13 | 6 | 1 | -2 | 3 | 4 | 7 | 6 | 5
62 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 48 | 47 | 46 | 45 | 42 | 39 | 36 | 33 | 30 |  |  | 221 | 24 | 62 | 27 | 29 | 24 | 23 | 24 | 22 | 19 | 14 | 7 | 2 | -1 | 4 | 5 | 8 | 7 | 6
63 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 47 | 46 | 45 | 44 | 41 | 38 | 35 | 32 | 29 |  |  | 236 | 25 | 63 | 28 | 30 | 25 | 24 | 25 | 23 | 20 | 15 | 8 | 3 | 0 | 5 | 6 | 9 | 8 | 7
64 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 46 | 45 | 44 | 43 | 40 | 37 | 34 | 31 | 28 |  |  | 252 | 26 | 64 | 29 | 31 | 26 | 25 | 26 | 24 | 21 | 16 | 9 | 4 | 1 | 6 | 7 | 10 | 9 | 8
65 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 45 | 44 | 43 | 42 | 39 | 36 | 33 | 30 | 27 |  |  | 268 | 27 | 65 | 30 | 32 | 27 | 26 | 27 | 25 | 22 | 17 | 10 | 5 | 2 | 7 | 8 | 11 | 10 | 9
66 | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 44 | 43 | 42 | 41 | 38 | 35 | 32 | 29 | 26 |  |  | 284 | 28 | 66 | 31 | 33 | 28 | 27 | 28 | 26 | 23 | 18 | 11 | 6 | 3 | 8 | 9 | 12 | 11 | 10
67 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 43 | 42 | 41 | 40 | 37 | 34 | 31 | 28 | 25 |  |  | 300 | 29 | 67 | 32 | 34 | 29 | 28 | 29 | 27 | 24 | 19 | 12 | 7 | 4 | 9 | 10 | 13 | 12 | 11
68 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 42 | 41 | 40 | 39 | 36 | 33 | 30 | 27 | 24 |  |  | 316 | 30 | 68 | 33 | 35 | 30 | 29 | 30 | 28 | 25 | 20 | 13 | 8 | 5 | 10 | 11 | 14 | 13 | 12
69 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 41 | 40 | 39 | 38 | 35 | 32 | 29 | 26 | 23 |  |  | 332 | 31 | 69 | 34 | 36 | 31 | 30 | 31 | 29 | 26 | 21 | 14 | 9 | 6 | 11 | 12 | 15 | 14 | 13
70 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 40 | 39 | 38 | 37 | 34 | 31 | 28 | 25 | 22 |  |  | 348 | 32 | 70 | 35 | 37 | 32 | 31 | 32 | 30 | 27 | 22 | 15 | 10 | 7 | 12 | 13 | 16 | 15 | 14
71 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 39 | 38 | 37 | 36 | 33 | 30 | 27 | 24 | 21 |  |  | 364 | 33 | 71 | 36 | 38 | 33 | 32 | 33 | 31 | 28 | 23 | 16 | 11 | 8 | 13 | 14 | 17 | 16 | 15
72 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 38 | 37 | 36 | 35 | 32 | 29 | 26 | 23 | 20 |  |  | 380 | 34 | 72 | 37 | 39 | 34 | 33 | 34 | 32 | 29 | 24 | 17 | 12 | 9 | 14 | 15 | 18 | 17 | 16
73 | 39 | 39 | 39 | 39 | 39 | 39 | 38 | 37 | 36 | 35 | 34 | 31 | 28 | 25 | 22 | 19 |  |  | 396 | 35 | 73 | 38 | 40 | 35 | 34 | 35 | 33 | 30 | 25 | 18 | 13 | 10 | 15 | 16 | 19 | 18 | 17
74 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 36 | 35 | 34 | 33 | 30 | 27 | 24 | 21 | 18 |  |  | 412 | 36 | 74 | 39 | 41 | 36 | 35 | 36 | 34 | 31 | 26 | 19 | 14 | 11 | 16 | 17 | 20 | 19 | 18
75 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 35 | 34 | 33 | 32 | 29 | 26 | 23 | 20 | 17 |  |  | 428 | 37 | 75 | 40 | 42 | 37 | 36 | 37 | 35 | 32 | 27 | 20 | 15 | 12 | 17 | 18 | 21 | 20 | 19
76 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 34 | 33 | 32 | 31 | 28 | 25 | 22 | 19 | 16 |  |  | 444 | 38 | 76 | 41 | 43 | 38 | 37 | 38 | 36 | 33 | 28 | 21 | 16 | 13 | 18 | 19 | 22 | 21 | 20
77 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 33 | 32 | 31 | 30 | 27 | 24 | 21 | 18 | 15 |  |  | 460 | 39 | 77 | 42 | 44 | 39 | 38 | 39 | 37 | 34 | 29 | 22 | 17 | 14 | 19 | 20 | 23 | 22 | 21
78 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 32 | 31 | 30 | 29 | 26 | 23 | 20 | 17 | 14 |  |  | 476 | 40 | 78 | 43 | 45 | 40 | 39 | 40 | 38 | 35 | 30 | 23 | 18 | 15 | 20 | 21 | 24 | 23 | 22
79 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 31 | 30 | 29 | 28 | 25 | 22 | 19 | 16 | 13 |  |  | 492 | 41 | 79 | 44 | 46 | 41 | 40 | 41 | 39 | 36 | 31 | 24 | 19 | 16 | 21 | 22 | 25 | 24 | 23
80 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 30 | 29 | 28 | 27 | 24 | 21 | 18 | 15 | 12 |  |  | 508 | 42 | 80 | 45 | 47 | 42 | 41 | 42 | 40 | 37 | 32 | 25 | 20 | 17 | 22 | 23 | 26 | 25 | 24
81 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 29 | 28 | 27 | 26 | 23 | 20 | 17 | 14 | 11 |  |  | 524 | 43 | 81 | 46 | 48 | 43 | 42 | 43 | 41 | 38 | 33 | 26 | 21 | 18 | 23 | 24 | 27 | 26 | 25
82 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 28 | 27 | 26 | 25 | 22 | 19 | 16 | 13 | 10 |  |  | 540 | 44 | 82 | 47 | 49 | 44 | 43 | 44 | 42 | 39 | 34 | 27 | 22 | 19 | 24 | 25 | 28 | 27 | 26
83 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 27 | 26 | 25 | 24 | 21 | 18 | 15 | 12 | 9 |  |  | 556 | 45 | 83 | 48 | 50 | 45 | 44 | 45 | 43 | 40 | 35 | 28 | 23 | 20 | 25 | 26 | 29 | 28 | 27
84 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 26 | 25 | 24 | 23 | 20 | 17 | 14 | 11 | 8 |  |  | 572 | 46 | 84 | 49 | 51 | 46 | 45 | 46 | 44 | 41 | 36 | 29 | 24 | 21 | 26 | 27 | 30 | 29 | 28
85 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 25 | 24 | 23 | 22 | 19 | 16 | 13 | 10 | 7 |  |  | 588 | 47 | 85 | 50 | 52 | 47 | 46 | 47 | 45 | 42 | 37 | 30 | 25 | 22 | 27 | 28 | 31 | 30 | 29
86 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 24 | 23 | 22 | 21 | 18 | 15 | 12 | 9 | 6 |  |  | 604 | 48 | 86 | 51 | 53 | 48 | 47 | 48 | 46 | 43 | 38 | 31 | 26 | 23 | 28 | 29 | 32 | 31 | 30
87 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 23 | 22 | 21 | 20 | 17 | 14 | 11 | 8 | 5 |  |  | 620 | 49 | 87 | 52 | 54 | 49 | 48 | 49 | 47 | 44 | 39 | 32 | 27 | 24 | 29 | 30 | 33 | 32 | 31
88 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 22 | 21 | 20 | 19 | 16 | 13 | 10 | 7 | 4 |  |  | 636 | 50 | 88 | 53 | 55 | 50 | 49 | 50 | 48 | 45 | 40 | 33 | 28 | 25 | 30 | 31 | 34 | 33 | 32
89 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 21 | 20 | 19 | 18 | 15 | 12 | 9 | 6 | 3 |  |  | 652 | 51 | 89 | 54 | 56 | 51 | 50 | 51 | 49 | 46 | 41 | 34 | 29 | 26 | 31 | 32 | 35 | 34 | 33
90 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 19 | 18 | 17 | 14 | 11 | 8 | 5 | 2 |  |  | 668 | 52 | 90 | 55 | 57 | 52 | 51 | 52 | 50 | 47 | 42 | 35 | 30 | 27 | 32 | 33 | 36 | 35 | 34
91 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 19 | 18 | 17 | 16 | 13 | 10 | 7 | 4 | 1 |  |  | 684 | 53 | 91 | 56 | 58 | 53 | 52 | 53 | 51 | 48 | 43 | 36 | 31 | 28 | 33 | 34 | 37 | 36 | 35
92 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 18 | 17 | 16 | 15 | 12 | 9 | 6 | 3 | 0 |  |  | 700 | 54 | 92 | 57 | 59 | 54 | 53 | 54 | 52 | 49 | 44 | 37 | 32 | 29 | 34 | 35 | 38 | 37 | 36
93 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 17 | 16 | 15 | 14 | 11 | 8 | 5 | 2 | -1 |  |  | 716 | 55 | 93 | 58 | 60 | 55 | 54 | 55 | 53 | 50 | 45 | 38 | 33 | 30 | 35 | 36 | 39 | 38 | 37
94 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 16 | 15 | 14 | 13 | 10 | 7 | 4 | 1 | -2 |  |  | 732 | 56 | 94 | 59 | 61 | 56 | 55 | 56 | 54 | 51 | 46 | 39 | 34 | 31 | 36 | 37 | 40 | 39 | 38
95 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 15 | 14 | 13 | 12 | 9 | 6 | 3 | 0 | -3 |  |  | 748 | 57 | 95 | 60 | 62 | 57 | 56 | 57 | 55 | 52 | 47 | 40 | 35 | 32 | 37 | 38 | 41 | 40 | 39
96 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 14 | 13 | 12 | 11 | 8 | 5 | 2 | -1 | -4 |  |  | 764 | 58 | 96 | 61 | 63 | 58 | 57 | 58 | 56 | 53 | 48 | 41 | 36 | 33 | 38 | 39 | 42 | 41 | 40
97 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 13 | 12 | 11 | 10 | 7 | 4 | 1 | -2 | -5 |  |  | 780 | 59 | 97 | 62 | 64 | 59 | 58 | 59 | 57 | 54 | 49 | 42 | 37 | 34 | 39 | 40 | 43 | 42 | 41
98 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 12 | 11 | 10 | 9 | 6 | 3 | 0 | -3 | -6 |  |  | 796 | 60 | 98 | 63 | 65 | 60 | 59 | 60 | 58 | 55 | 50 | 43 | 38 | 35 | 40 | 41 | 44 | 43 | 42
99 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 11 | 10 | 9 | 8 | 5 | 2 | -1 | -4 | -7 |  |  | 812 | 61 | 99 | 64 | 66 | 61 | 60 | 61 | 59 | 56 | 51 | 44 | 39 | 36 | 41 | 42 | 45 | 44 | 43
100 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 10 | 9 | 8 | 7 | 4 | 1 | -2 | -5 | -8 |  |  | 828 | 62 | 100 | 65 | 67 | 62 | 61 | 62 | 60 | 57 | 52 | 45 | 40 | 37 | 42 | 43 | 46 | 45 | 44

## Old Report (hidden)
Report Date: | 2024-04-18
Test Date: | 2024-04-04
Test Site: | Ka'ulu by Gentry
Test Construction: | Floor-ceiling
DLAA Test #: | 1.2.1
Conducted For: | Gentry Builders, LLC
STATEMENT OF CONFORMANCE TO STANDARD:
Testing was conducted in general accordance with ASTM Designation E 336-11, Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings, except that flanking sound was not eliminated in accordance with the procedures of Annex A1, Measurement of Field Transmission Loss. The measurements were used to calculate Apparent Sound Transmission Class (ASTC) in accordance with ASTM Designation E 413 - 10, Classification for Rating Sound Insulation. The procedures of Section 11 were performed. The procedures of Annex 2 were not used. |  | Testing was conducted in general accordance with ASTM Designation E 336-11, Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings, except that flanking sound was not eliminated in accordance with the procedures of Annex A1, Measurement of Field Transmission Loss. The measurements were used to calculate Apparent Sound Transmission Class (ASTC) in accordance with ASTM Designation E 413 - 10, Classification for Rating Sound Insulation. The procedures of Section 11 were performed. The procedures of Annex 2 were not used.
TEST ENVIRONMENT
REFERENCES
ASTM E336-11, Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings
ASTM E413-10, Classification for Rating Sound Insulation
ASTM E2235-04 (2012), Standard Test Method for Determination of Decay Rates for Use in Sound Insulation Test Methods
TEST INSTRUMENTATION
Tapping Machine: | Norsonics NOR277 Tapping Machine, SN. 2775671
Last Calibration – September 2012
Sound Level Meter: | Larson Davis Model 831, SN. 2237
Last NIST Traceable Calibration August 2012
Last Local Calibration, May 14, 2013
Larson Davis Microphone 377B20, SN LW130096
Last NIST Traceable Calibration July 2012
Larson Davis Preamplifier Model PRM831 SN 16913
Last NIST Traceable Calibration August 2012
Calibrator: | Larson Davis CAL200, Serial No. 2442
Last NIST Traceable Calibration August 2012
STATEMENT OF TEST RESULTS
APPARENT SOUND TRANSMISSION CLASS

## Transpose
Frequency | Average Source Room Level (dB) | Average Corrected Receiver Room Level (dB) | Average Receiver Background Level | Avgerage RT60 | Noise Reduction, NR (dB) | Apparent Transmission Loss, ATL (dB) | Impact Sound Pressure Level, ISPL (dB) | Absorption Normalized Impact Sound Pressure Level, ANISPL (dB) | ASTC 41 Contour | NIC 39 Contour | AIIC 38 Contour | ISR 42 Contour | STC: 5 dB Background Check | IIC: 5 dB Background Check | IIC: 10 dB Sound Flanking Check
100 | 95.8 | 78.2 | 35.4 | 0.61783 | 17.6 | 19 | 77.134 | 82 |  |  | 74 | 70 | pass | pass | pass
125 | 95 | 79.5 | 39.2 | 0.84579 | 15.5 | 18.2 | 79.2538 | 83 | 25 | 23 | 74 | 70 | pass | pass | pass
160 | 91.4 | 73 | 33 | 0.63261 | 18.4 | 19.9 | 74.4402 | 79 | 28 | 26 | 74 | 70 | pass | pass | pass
200 | 90 | 65.6 | 37.1 | 0.99566 | 24.4 | 27.8 | 73.2975 | 76 | 31 | 29 | 74 | 70 | pass | pass | pass
250 | 91.6 | 61.6 | 34.4 | 1.0232 | 30 | 33.5 | 74.3392 | 77 | 34 | 32 | 74 | 70 | pass | pass | pass
315 | 89.7 | 57.6 | 33.7 | 1.1372 | 32.1 | 36.1 | 71.611 | 74 | 37 | 35 | 74 | 70 | pass | pass | pass
400 | 88.8 | 52.7 | 33.3 | 1.3446 | 36.1 | 40.8 | 67.6428 | 69 | 40 | 38 | 73 | 69 | pass | pass | pass
500 | 84.7 | 47.5 | 32.5 | 1.2621 | 37.2 | 41.7 | 61.7255 | 63 | 41 | 39 | 72 | 68 | pass | pass | pass
630 | 82.5 | 42 | 31.2 | 1.1412 | 40.5 | 44.5 | 54.3417 | 56 | 42 | 40 | 71 | 67 | pass | pass | pass
800 | 84.5 | 39.9196 | 30.6 | 1.1179 | 44.6 | 48.5 | 48.3812 | 50 | 43 | 41 | 70 | 66 | pass | pass | pass
1000 | 83 | 33.6622 | 29.6 | 1.2872 | 49.3 | 53.9 | 44.3479 | 46 | 44 | 42 | 69 | 65 | pass | pass | pass
1250 | 83.8 | 30.4 | 28.9 | 1.4592 | 53.4 | 58.5 | 45.9783 | 47 | 45 | 43 | 66 | 62 | fail | pass | pass
1600 | 81.4 | 28.2 | 28.5 | 1.5181 | 53.2 | 58.5 | 43.8788 | 45 | 45 | 43 | 63 | 59 | fail | pass | pass
2000 | 79.8 | 25.5 | 24.9 | 1.4609 | 54.3 | 59.4 | 44.3888 | 45 | 45 | 43 | 60 | 56 | fail | pass | pass
2500 | 82.4 | 22.1 | 20.6 | 1.3927 | 60.3 | 65.2 | 39.6455 | 41 | 45 | 43 | 57 | 53 | fail | pass | pass
3150 | 84 | 19.6 | 18.5 | 1.4027 | 64.4 | 69.3 | 36.4536 | 38 | 45 | 43 | 54 | 50 | fail | pass | pass
4000 | 85 | 17.7 | 17.6 | 1.3876 | 67.3 | 72.2 | 32.5693 | 34 | 45 | 43 |  |  | fail
5000 | 84.3 | 16.1 | 15.1 | 1.3159 | 68.2 | 72.8 | 29.757 | 31 |  |  |  |  | fail

## NICReport
Frequency (Hz)
Report Date: | 2024-04-18 |  | Source Room: |  | 2nd Floor Kitchen, Volume: 3950 cu. ft. |  |  |  |  | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000
Test Date: | 2024-04-04 |  | Receiver Room: |  | 1st Floor Great Room/Kitchen, Volume: 3950 cu. ft. |  |  |  | Avg. Source Room Sound Pressure (dB) | 95.8 | 95 | 91.4 | 90 | 91.6 | 89.7 | 88.8 | 84.7 | 82.5 | 84.5 | 83 | 83.8 | 81.4 | 79.8 | 82.4 | 84 | 85 | 84.3
DLAA Test No: | 1.2.1 |  | Test Assembly: |  | Floor-ceiling, Area: 428 sq. ft. |  |  |  | Pink Noise Receiver Room | 78.2 | 79.5 | 73 | 65.6 | 61.6 | 57.6 | 52.7 | 47.5 | 42 | 40.4 | 35.1 | 32.4 | 30.2 | 27.5 | 24.1 | 21.6 | 19.7 | 18.1
[9 empty] | Receiver B.G. | 35.4 | 39.2 | 33 | 37.1 | 34.4 | 33.7 | 33.3 | 32.5 | 31.2 | 30.6 | 29.6 | 28.9 | 28.5 | 24.9 | 20.6 | 18.5 | 17.6 | 15.1
Test Site: | Ka'ulu by Gentry | [7 empty] | RT60 Average | 0.61783 | 0.84579 | 0.63261 | 0.99566 | 1.0232 | 1.1372 | 1.3446 | 1.2621 | 1.1412 | 1.1179 | 1.2872 | 1.4592 | 1.5181 | 1.4609 | 1.3927 | 1.4027 | 1.3876 | 1.3159
Client: | Gentry Builders, LLC
STANDARDS
ASTM E336-16 | Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings | [6 empty] | Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings
ASTM E413-16 | Classification for Rating Sound Insulation | [6 empty] | ASTM E413-16
ASTM E2235-04(2012) | Standard Test Method for Determination of Decay Rates for Use in Sound Insulation Test Methods | [6 empty] | ASTM E2235-04(2012)
STATEMENT OF CONFORMANCE:
Testing was conducted in general accordance with ASTM E336-16, with all exceptions noted below. The requirements for measuring and reporting Absorption Normalized Impact Sound Pressure Levels (ANISPL) and Apparent Impact Insulation Class (AIIC) were not met, therefore only Impact Sound Pressure Level (ISPL) and Impact Sound Rating (ISR) have been reported. Exceptions to ASTM E336-16 that disallow reporting ATL and ASTC are as follows: | [7 empty] | Testing was conducted in general accordance with ASTM E336-16, with all exceptions noted below. The requirements for measuring and reporting Absorption Normalized Impact Sound Pressure Levels (ANISPL) and Apparent Impact Insulation Class (AIIC) were not met, therefore only Impact Sound Pressure Level (ISPL) and Impact Sound Rating (ISR) have been reported. Exceptions to ASTM E336-16 that disallow reporting ATL and ASTC are as follows:
--- | [7 empty] | ---
The procedures of ASTM E336-16 Annex were not used.
TEST ENVIRONMENT:
The source room was 2nd Floor Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The source room had a volume of approximately 3950 cu. ft. | [7 empty] | The source room was 2nd Floor Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The source room had a volume of approximately 3950 cu. ft.
The receiver room was 1st Floor Great Room/Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The receiver room had a volume of approximately 3949 cu. ft. | [7 empty] | The receiver room was 1st Floor Great Room/Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The receiver room had a volume of approximately 3949 cu. ft.
The test assembly measured approximately 14.8x29.583, and had an approximate area of 428 sq. ft. | [7 empty] | The test assembly measured approximately 14.8x29.583, and had an approximate area of 428 sq. ft.
TEST ASSEMBLY:
The tested assembly was the Floor-ceiling The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations. | [7 empty] | The tested assembly was the Floor-ceiling The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations.
TEST PROCEDURE:
Determination of space-average sound pressure levels was performed via the manually scanned microphones techique, described in ASTM E336-16, Paragraph 11.4.3.3. | [7 empty] | Determination of space-average sound pressure levels was performed via the manually scanned microphones techique, described in ASTM E336-16, Paragraph 11.4.3.3.
The source room was selected in accordance with ASTM E336-11 Paragraph 9.2.5, which states that "If a corridor must be used as one of the spaces for measurement of ATL or FTL, it shall be used as the source space." | [7 empty] | The source room was selected in accordance with ASTM E336-11 Paragraph 9.2.5, which states that "If a corridor must be used as one of the spaces for measurement of ATL or FTL, it shall be used as the source space."
Flanking transmission was not evaluated.
To evaluate room absorption, 1 microphone was used to measure 4 decays at 4 locations around the receiving room for a total of 16 measurements, per ASTM E2235-04(2012). | [7 empty] | To evaluate room absorption, 1 microphone was used to measure 4 decays at 4 locations around the receiving room for a total of 16 measurements, per ASTM E2235-04(2012).
TEST INSTRUMENTATION:
Equipment Type | Manufacturer | Model Number | Serial Number |  | Last NIST Traceable Calibration | Last Local Calibration
Sound Level Meter 1 | Larson Davis | 831 | 3784 |  | 2022-09-19 | 2024-04-04
Microphone Pre-Amp: | Larson Davis | PRM831 | 51188 |  | 2022-09-19 | 2024-04-04
Microphone: | Larson Davis | 377B20 | 301698 |  | 2022-09-16 | 2024-04-04
Calibrator: | Larson Davis | CAL200 | 2775671 |  | 2022-09-19 | N/A
Sound Level Meter 2 | Larson Davis | 831 | 4328 |  | 2022-10-24 | 2024-04-04
Microphone Pre-Amp: | Larson Davis | PRM831 | 046469 |  | 2022-10-24 | 2024-04-04
Microphone: | Larson Davis | 377B20 | 168830 |  | 2022-10-20 | 2024-04-04
Calibrator: | Larson Davis | CAL200 | 5955 |  | 2022-10-26 | N/A
Amplified Loudspeakers (QTY 2) | QSC | K10 | GAA530909 |  | N/A | N/A
Noise Generator: | NTi Audio | MR-PRO | 0162 |  | N/A | N/A
STATEMENT OF TEST RESULTS:
Frequency | L1, Average Source Room Level (dB) | L2, Average Corrected Receiver Room Level (dB) | Average Receiver Background Level (dB) | Noise Reduction, NR (dB)
100 | 95.8 | 78.2 | 35.4 | 17.6
125 | 95 | 79.5 | 39.2 | 15.5
160 | 91.4 | 73 | 33 | 18.4
200 | 90 | 65.6 | 37.1 | 24.4
250 | 91.6 | 61.6 | 34.4 | 30
315 | 89.7 | 57.6 | 33.7 | 32.1
400 | 88.8 | 52.7 | 33.3 | 36.1
500 | 84.7 | 47.5 | 32.5 | 37.2
630 | 82.5 | 42 | 31.2 | 40.5
800 | 84.5 | 39.9196 | 30.6 | 44.6
1000 | 83 | 33.6622 | 29.6 | 49.3
1250 | 83.8 | 30.4 | 28.9 | 53.4
1600 | 81.4 | 28.2 | 28.5 | 53.2
2000 | 79.8 | 25.5 | 24.9 | 54.3
2500 | 82.4 | 22.1 | 20.6 | 60.3
3150 | 84 | 19.6 | 18.5 | 64.4
4000 | 85 | 17.7 | 17.6 | 67.3
5000 | 84.3 | 16.1 | 15.1 | 68.2
0
NIC: 39
A Noise Isolation Class (NIC) of 39 was calculated. The NIC rating is based on Noise Reduction (NR), and includes the effects of noise flanking. The NIC reference contour is shown on the next page, and has been “fit” to the Apparent Transmission Loss values, in accordance with the procedure of ASTC Test Procedure. | [7 empty] | A Noise Isolation Class (NIC) of 39 was calculated. The NIC rating is based on Noise Reduction (NR), and includes the effects of noise flanking. The NIC reference contour is shown on the next page, and has been “fit” to the Apparent Transmission Loss values, in accordance with the procedure of ASTC Test Procedure.
The results stated in this report represent only the specific construction and acoustical conditions present at the time of the test. Measurements performed in accordance with this test method on nominally identical constructions and acoustical conditions may produce different results. | [7 empty] | The results stated in this report represent only the specific construction and acoustical conditions present at the time of the test. Measurements performed in accordance with this test method on nominally identical constructions and acoustical conditions may produce different results.
NIC: 39
Test Conducted By:
Zane Wright, Project Consultant |  |  |  |  | Jake Pfitsch, Project Consultant

## ASTC Report
Frequency (Hz)
Report Date: | 2024-04-18 |  | Source Room: |  | 2nd Floor Kitchen, Volume: 3950 cu. ft. | [5 empty] | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000
Test Date: | 2024-04-04 |  | Receiver Room: |  | 1st Floor Great Room/Kitchen, Volume: 3950 cu. ft. |  |  |  |  | Avg. Source Room Sound Pressure (dB) | 95.8 | 95 | 91.4 | 90 | 91.6 | 89.7 | 88.8 | 84.7 | 82.5 | 84.5 | 83 | 83.8 | 81.4 | 79.8 | 82.4 | 84 | 85 | 84.3
DLAA Test No: | 1.2.1 |  | Test Assembly: |  | Floor-ceiling, Area: 428 sq. ft. |  |  |  |  | Pink Noise Receiver Room | 78.2 | 79.5 | 73 | 65.6 | 61.6 | 57.6 | 52.7 | 47.5 | 42 | 40.4 | 35.1 | 32.4 | 30.2 | 27.5 | 24.1 | 21.6 | 19.7 | 18.1
[10 empty] | Receiver B.G. | 35.4 | 39.2 | 33 | 37.1 | 34.4 | 33.7 | 33.3 | 32.5 | 31.2 | 30.6 | 29.6 | 28.9 | 28.5 | 24.9 | 20.6 | 18.5 | 17.6 | 15.1
Test Site: | Ka'ulu by Gentry | [8 empty] | RT60 Average | 0.61783 | 0.84579 | 0.63261 | 0.99566 | 1.0232 | 1.1372 | 1.3446 | 1.2621 | 1.1412 | 1.1179 | 1.2872 | 1.4592 | 1.5181 | 1.4609 | 1.3927 | 1.4027 | 1.3876 | 1.3159
Client: | Gentry Builders, LLC
STANDARDS
ASTM E336-16 | Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings | [7 empty] | Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings
ASTM E413-16 | Classification for Rating Sound Insulation | [7 empty] | ASTM E413-16
ASTM E2235-04(2012) | Standard Test Method for Determination of Decay Rates for Use in Sound Insulation Test Methods | [7 empty] | ASTM E2235-04(2012)
STATEMENT OF CONFORMANCE:
Testing was conducted in general accordance with ASTM E336-16, with all exceptions noted below. All requirements for measuring and reporting Apparent Transmission Loss (ATL) and Apparent Sound Transmission Class (ASTC) were met. | [8 empty] | Testing was conducted in general accordance with ASTM E336-16, with all exceptions noted below. All requirements for measuring and reporting Apparent Transmission Loss (ATL) and Apparent Sound Transmission Class (ASTC) were met.
The procedures of ASTM E336-16 Annex were not used.
TEST ENVIRONMENT:
The source room was 2nd Floor Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The source room had a volume of approximately 3950 cu. ft. | [8 empty] | The source room was 2nd Floor Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The source room had a volume of approximately 3950 cu. ft.
The receiver room was 1st Floor Great Room/Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The receiver room had a volume of approximately 3950 cu. ft. | [8 empty] | The receiver room was 1st Floor Great Room/Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The receiver room had a volume of approximately 3950 cu. ft.
The test assembly measured approximately 14.8x29.583, and had an approximate area of 428 sq. ft. | [8 empty] | The test assembly measured approximately 14.8x29.583, and had an approximate area of 428 sq. ft.
TEST ASSEMBLY:
The tested assembly was the Floor-ceiling The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations. | [8 empty] | The tested assembly was the Floor-ceiling The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations.
TEST PROCEDURE:
Determination of space-average sound pressure levels was performed via the manually scanned microphones techique, described in ASTM E336-16, Paragraph 11.4.3.3. | [8 empty] | Determination of space-average sound pressure levels was performed via the manually scanned microphones techique, described in ASTM E336-16, Paragraph 11.4.3.3.
Flanking transmission was not evaluated.
To evaluate room absorption, 1 microphone was used to measure 4 decays at 4 locations around the receiving room for a total of 16 measurements, per ASTM E2235-04(2012). | [8 empty] | To evaluate room absorption, 1 microphone was used to measure 4 decays at 4 locations around the receiving room for a total of 16 measurements, per ASTM E2235-04(2012).
TEST INSTRUMENTATION:
Equipment Type | Manufacturer | Model Number | Serial Number |  | Last NIST Traceable Calibration | Last Local Calibration
Sound Level Meter 1 | Larson Davis | 831 | 3784 |  | 2022-09-19 | 2024-04-04
Microphone Pre-Amp: | Larson Davis | PRM831 | 051188 |  | 2022-09-19 | 2024-04-04
Microphone: | Larson Davis | 377B20 | 301698 |  | 2022-09-16 | 2024-04-04
Calibrator: | Larson Davis | CAL200 | 2775671 |  | 2022-09-19 | N/A
Sound Level Meter 2 | Larson Davis | 831 | 4328 |  | 2022-10-24 | 2024-04-04
Microphone Pre-Amp: | Larson Davis | PRM831 | 046469 |  | 2022-10-24 | 2024-04-04
Microphone: | Larson Davis | 377B20 | 168830 |  | 2022-10-20 | 2024-04-04
Calibrator: | Larson Davis | CAL200 | 5955 |  | 2022-10-26 | N/A
Amplified Loudspeakers (QTY 2) | QSC | K10 | GAA530909 |  | N/A | N/A
Noise Generator: | NTi Audio | MR-PRO | 0162 |  | N/A | N/A
STATEMENT OF TEST RESULTS:
Frequency | L1, Average Source Room Level (dB) | L2, Average Corrected Receiver Room Level (dB) | Average Receiver Background Level (dB) | Average RT60 (Seconds) | Noise Reduction, NR (dB) | Apparent Transmission Loss, ATL (dB) | Exceptions noted to ASTM E336-16
100 | 95.8 | 78.2 | 35.4 | 0.61783 | 17.6 | 19
125 | 95 | 79.5 | 39.2 | 0.84579 | 15.5 | 18.2
160 | 91.4 | 73 | 33 | 0.63261 | 18.4 | 19.9
200 | 90 | 65.6 | 37.1 | 0.99566 | 24.4 | 27.8
250 | 91.6 | 61.6 | 34.4 | 1.0232 | 30 | 33.5
315 | 89.7 | 57.6 | 33.7 | 1.1372 | 32.1 | 36.1
400 | 88.8 | 52.7 | 33.3 | 1.3446 | 36.1 | 40.8
500 | 84.7 | 47.5 | 32.5 | 1.2621 | 37.2 | 41.7
630 | 82.5 | 42 | 31.2 | 1.1412 | 40.5 | 44.5
800 | 84.5 | 39.9196 | 30.6 | 1.1179 | 44.6 | 48.5
1000 | 83 | 33.6622 | 29.6 | 1.2872 | 49.3 | 53.9
1250 | 83.8 | 30.4 | 28.9 | 1.4592 | 53.4 | 58.5
1600 | 81.4 | 28.2 | 28.5 | 1.5181 | 53.2 | 58.5
2000 | 79.8 | 25.5 | 24.9 | 1.4609 | 54.3 | 59.4
2500 | 82.4 | 22.1 | 20.6 | 1.3927 | 60.3 | 65.2
3150 | 84 | 19.6 | 18.5 | 1.4027 | 64.4 | 69.3
4000 | 85 | 17.7 | 17.6 | 1.3876 | 67.3 | 72.2
5000 | 84.3 | 16.1 | 15.1 | 1.3159 | 68.2 | 72.8
0
ASTC: 41
An Apparent Sound Transmission Class (ASTC) of 41, and a Noise Isolation Class (NIC) of 39 was calculated. The NIC rating is based on Noise Reduction (NR), and includes the effects of noise flanking. The NIC reference contour is shown on the next page, and has been “fit” to the Apparent Transmission Loss values, in accordance with the procedure of ASTM E413-16. | [8 empty] | An Apparent Sound Transmission Class (ASTC) of 41, and a Noise Isolation Class (NIC) of 39 was calculated. The NIC rating is based on Noise Reduction (NR), and includes the effects of noise flanking. The NIC reference contour is shown on the next page, and has been “fit” to the Apparent Transmission Loss values, in accordance with the procedure of ASTM E413-16.
The results stated in this report represent only the specific construction and acoustical conditions present at the time of the test. Measurements performed in accordance with this test method on nominally identical constructions and acoustical conditions may produce different results. | [8 empty] | The results stated in this report represent only the specific construction and acoustical conditions present at the time of the test. Measurements performed in accordance with this test method on nominally identical constructions and acoustical conditions may produce different results.
ASTC: 41
Test Conducted By:
Zane Wright, Project Consultant |  |  |  |  | Jake Pfitsch, Project Consultant

## NIC Report (hidden)
Frequency (Hz)
Report Date: | 2024-04-18 |  | Source Room: |  | 2nd Floor Kitchen, Volume: 3950 cu. ft. |  |  |  |  | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000
Test Date: | 2024-04-04 |  | Receiver Room: |  | 1st Floor Great Room/Kitchen, Volume: 3950 cu. ft. |  |  |  | Avg. Source Room Sound Pressure (dB) | 95.8 | 95 | 91.4 | 90 | 91.6 | 89.7 | 88.8 | 84.7 | 82.5 | 84.5 | 83 | 83.8 | 81.4 | 79.8 | 82.4 | 84 | 85 | 84.3
DLAA Test No: | 1.2.1 |  | Test Assembly: |  | Floor-ceiling, Area: 428 sq. ft. |  |  |  | Pink Noise Receiver Room | 78.2 | 79.5 | 73 | 65.6 | 61.6 | 57.6 | 52.7 | 47.5 | 42 | 40.4 | 35.1 | 32.4 | 30.2 | 27.5 | 24.1 | 21.6 | 19.7 | 18.1
[9 empty] | Receiver B.G. | 35.4 | 39.2 | 33 | 37.1 | 34.4 | 33.7 | 33.3 | 32.5 | 31.2 | 30.6 | 29.6 | 28.9 | 28.5 | 24.9 | 20.6 | 18.5 | 17.6 | 15.1
Test Site: | Ka'ulu by Gentry | [7 empty] | RT60 Average | 0.61783 | 0.84579 | 0.63261 | 0.99566 | 1.0232 | 1.1372 | 1.3446 | 1.2621 | 1.1412 | 1.1179 | 1.2872 | 1.4592 | 1.5181 | 1.4609 | 1.3927 | 1.4027 | 1.3876 | 1.3159
Client: | Gentry Builders, LLC
STANDARDS
ASTM E336-16 | Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings | [6 empty] | Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings
ASTM E413-16 | Classification for Rating Sound Insulation | [6 empty] | ASTM E413-16
ASTM E2235-04(2012) | Standard Test Method for Determination of Decay Rates for Use in Sound Insulation Test Methods | [6 empty] | ASTM E2235-04(2012)
STATEMENT OF CONFORMANCE:
Testing was conducted in general accordance with ASTM E336-16, with all exceptions noted below. The requirements for measuring and reporting Apparent Transmission Loss (ATL) and Apparent Sound Transmission Class (ASTC) were not met, therefore only Noise Reduction (NR) and Noise Isolation Class (NIC) have been reported. Exceptions to ASTM E336-16 that disallow reporting ATL and ASTC are as follows: | [7 empty] | Testing was conducted in general accordance with ASTM E336-16, with all exceptions noted below. The requirements for measuring and reporting Apparent Transmission Loss (ATL) and Apparent Sound Transmission Class (ASTC) were not met, therefore only Noise Reduction (NR) and Noise Isolation Class (NIC) have been reported. Exceptions to ASTM E336-16 that disallow reporting ATL and ASTC are as follows:
0 | [7 empty] | 0
The procedures of ASTM E336-16 Annex 1 and Annex 2 were not used.
TEST ENVIRONMENT:
The source room was 2nd Floor Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The source room had a volume of approximately 3950 cu. ft. | [7 empty] | The source room was 2nd Floor Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The source room had a volume of approximately 3950 cu. ft.
The receiver room was 1st Floor Great Room/Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The receiver room had a volume of approximately 3950 cu. ft. | [7 empty] | The receiver room was 1st Floor Great Room/Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The receiver room had a volume of approximately 3950 cu. ft.
The test assembly measured approximately 14.8x29.583, and had an approximate area of 428 sq. ft. | [7 empty] | The test assembly measured approximately 14.8x29.583, and had an approximate area of 428 sq. ft.
TEST ASSEMBLY:
The tested assembly was the Floor-ceiling The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations. | [7 empty] | The tested assembly was the Floor-ceiling The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations.
TEST PROCEDURE:
Determination of space-average sound pressure levels was performed via the manually scanned microphones techique, described in ASTM E336-16, Paragraph 11.4.3.3. | [7 empty] | Determination of space-average sound pressure levels was performed via the manually scanned microphones techique, described in ASTM E336-16, Paragraph 11.4.3.3.
The source room was selected in accordance with ASTM E336-11 Paragraph 9.2.5, which states that "If a corridor must be used as one of the spaces for measurement of ATL or FTL, it shall be used as the source space." | [7 empty] | The source room was selected in accordance with ASTM E336-11 Paragraph 9.2.5, which states that "If a corridor must be used as one of the spaces for measurement of ATL or FTL, it shall be used as the source space."
Flanking transmission was not evaluated.
To evaluate room absorption, 1 microphone was used to measure 4 decays at 4 locations around the receiving room for a total of 16 measurements, per ASTM E2235-04(2012). | [7 empty] | To evaluate room absorption, 1 microphone was used to measure 4 decays at 4 locations around the receiving room for a total of 16 measurements, per ASTM E2235-04(2012).
TEST INSTRUMENTATION:
Equipment Type | Manufacturer | Model Number | Serial Number |  | Last NIST Traceable Calibration | Last Local Calibration
Sound Level Meter | Larson Davis | 831 | 3784 |  | 2022-09-19 | 2024-04-04
Microphone Pre-Amp | Larson Davis | PRM831 | 051188 |  | 2022-09-19 | 2024-04-04
Microphone | Larson Davis | 377B20 | 301698 |  | 2022-09-16 | 2024-04-04
Calibrator: | Larson Davis | CAL200 | #REF! |  | #REF! | N/A
Amplified Loudspeakers (QTY 2) | QSC | K10 | GAA530909 |  | N/A | N/A
Noise Generator: | NTi Audio | MR-PRO | 0162 |  | N/A | N/A
STATEMENT OF TEST RESULTS:
Frequency | L1, Average Source Room Level (dB) | L2, Average Corrected Receiver Room Level (dB) | Average Receiver Background Level (dB) | Average RT60 (Seconds) | Noise Reduction, NR (dB) | Exceptions noted to ASTM E336-16
100 | 95.8 | 78.2 | 35.4 | 0.61783 | 17.6
125 | 95 | 79.5 | 39.2 | 0.84579 | 15.5
160 | 91.4 | 73 | 33 | 0.63261 | 18.4
200 | 90 | 65.6 | 37.1 | 0.99566 | 24.4
250 | 91.6 | 61.6 | 34.4 | 1.0232 | 30
315 | 89.7 | 57.6 | 33.7 | 1.1372 | 32.1
400 | 88.8 | 52.7 | 33.3 | 1.3446 | 36.1
500 | 84.7 | 47.5 | 32.5 | 1.2621 | 37.2
630 | 82.5 | 42 | 31.2 | 1.1412 | 40.5
800 | 84.5 | 39.9196 | 30.6 | 1.1179 | 44.6
1000 | 83 | 33.6622 | 29.6 | 1.2872 | 49.3
1250 | 83.8 | 30.4 | 28.9 | 1.4592 | 53.4 | 1
1600 | 81.4 | 28.2 | 28.5 | 1.5181 | 53.2 | 1
2000 | 79.8 | 25.5 | 24.9 | 1.4609 | 54.3 | 1
2500 | 82.4 | 22.1 | 20.6 | 1.3927 | 60.3 | 1
3150 | 84 | 19.6 | 18.5 | 1.4027 | 64.4 | 1
4000 | 85 | 17.7 | 17.6 | 1.3876 | 67.3 | 1
5000 | 84.3 | 16.1 | 15.1 | 1.3159 | 68.2 | 1
7
*This test does not fully conform to the requirements of ASTM E336-11, so the calculated NIC rating should be considered a minimum. Notes: |  |  |  |  | NIC: 39 |  |  | *This test does not fully conform to the requirements of ASTM E336-11, so the calculated NIC rating should be considered a minimum. Notes:
1. The signal-to-noise ratio is less < 5 dB at this frequency band.
A Noise Isolation Class (NIC) of 39 was calculated. The NIC rating is based on Noise Reduction (NR), and includes the effects of noise flanking. The NIC reference contour is shown on the next page, and has been “fit” to the Apparent Transmission Loss values, in accordance with the procedure of ASTM E413-16. | [7 empty] | A Noise Isolation Class (NIC) of 39 was calculated. The NIC rating is based on Noise Reduction (NR), and includes the effects of noise flanking. The NIC reference contour is shown on the next page, and has been “fit” to the Apparent Transmission Loss values, in accordance with the procedure of ASTM E413-16.
The results stated in this report represent only the specific construction and acoustical conditions present at the time of the test. Measurements performed in accordance with this test method on nominally identical constructions and acoustical conditions may produce different results. | [7 empty] | The results stated in this report represent only the specific construction and acoustical conditions present at the time of the test. Measurements performed in accordance with this test method on nominally identical constructions and acoustical conditions may produce different results.
NIC: 39
Test Conducted By:
Zane Wright, Project Consultant |  |  |  |  | Jake Pfitsch, Project Consultant

## AIIC Report
Frequency (Hz)
Report Date: | 2024-04-18 |  | Source Room: |  | 2nd Floor Kitchen, Volume: 3949 cu. ft. |  |  |  |  | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000
Test Date: | 2024-04-04 |  | Receiver Room: |  | 1st Floor Great Room/Kitchen, Volume: 3949 cu. ft. |  |  |  | Avg. Source Room Sound Pressure (dB) | 95.8 | 95 | 91.4 | 90 | 91.6 | 89.7 | 88.8 | 84.7 | 82.5 | 84.5 | 83 | 83.8 | 81.4 | 79.8 | 82.4 | 84 | 85 | 84.3
DLAA Test No: | 1.2.1 |  | Test Assembly: |  | Floor-ceiling, Area: 428 sq. ft. |  |  |  | Pink Noise Receiver Room | 78.2 | 79.5 | 73 | 65.6 | 61.6 | 57.6 | 52.7 | 47.5 | 42 | 40.4 | 35.1 | 32.4 | 30.2 | 27.5 | 24.1 | 21.6 | 19.7 | 18.1
[9 empty] | Receiver B.G. | 35.4 | 39.2 | 33 | 37.1 | 34.4 | 33.7 | 33.3 | 32.5 | 31.2 | 30.6 | 29.6 | 28.9 | 28.5 | 24.9 | 20.6 | 18.5 | 17.6 | 15.1
Test Site: | Ka'ulu by Gentry | [7 empty] | RT60 Average | 0.61783 | 0.84579 | 0.63261 | 0.99566 | 1.0232 | 1.1372 | 1.3446 | 1.2621 | 1.1412 | 1.1179 | 1.2872 | 1.4592 | 1.5181 | 1.4609 | 1.3927 | 1.4027 | 1.3876 | 1.3159
Client: | Gentry Builders, LLC
STANDARDS
ASTM E1007-14 | Standard Test Method for Field Measurement of Tapping Machine Impact Sound Transmission Through Floor-Ceiling Assemblies and Associated Support Structure | [6 empty] | Standard Test Method for Field Measurement of Tapping Machine Impact Sound Transmission Through Floor-Ceiling Assemblies and Associated Support Structure
ASTM E989-06(2012) | Standard Classification for Determination of Impact Insulation Class (IIC) | [6 empty] | ASTM E989-06(2012)
ASTM E2235-04(2012) | Standard Test Method for Determination of Decay Rates for Use in Sound Insulation Test Methods | [6 empty] | ASTM E2235-04(2012)
STATEMENT OF CONFORMANCE:
Testing was conducted in general accordance with ASTM E1007-14, with all exceptions noted below. All requirements for measuring and reporting Absorption Normalized Impact Sound Pressure Level (ANISPL) and Apparent Impact Insulation Class (AIIC) were met. | [7 empty] | Testing was conducted in general accordance with ASTM E1007-14, with all exceptions noted below. All requirements for measuring and reporting Absorption Normalized Impact Sound Pressure Level (ANISPL) and Apparent Impact Insulation Class (AIIC) were met.
TEST ENVIRONMENT:
The source room was 2nd Floor Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The source room had a volume of approximately 3949 cu. ft. | [7 empty] | The source room was 2nd Floor Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The source room had a volume of approximately 3949 cu. ft.
The receiver room was 1st Floor Great Room/Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The receiver room had a volume of approximately 3949 cu. ft. | [7 empty] | The receiver room was 1st Floor Great Room/Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The receiver room had a volume of approximately 3949 cu. ft.
The test assembly measured approximately 14.8x29.583, and had an approximate area of 428 sq. ft. | [7 empty] | The test assembly measured approximately 14.8x29.583, and had an approximate area of 428 sq. ft.
TEST ASSEMBLY:
The tested assembly was the Floor-ceiling The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations. | [7 empty] | The tested assembly was the Floor-ceiling The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations.
TEST PROCEDURE:
The test was performaned in general accordance with ASTM E1007-14. Determination of Space-Average Levels performed via the manually scanned microphones techique, described in ASTM E1007-14, Paragraph 11.4.2.2. | [7 empty] | The test was performaned in general accordance with ASTM E1007-14. Determination of Space-Average Levels performed via the manually scanned microphones techique, described in ASTM E1007-14, Paragraph 11.4.2.2.
Flanking transmission was not evaluated.
To evaluate room absorption, 1 microphone was used to measure 4 decays at 4 locations around the receiving room for a total of 16 measurements, per ASTM E2235-04(2012). | [7 empty] | To evaluate room absorption, 1 microphone was used to measure 4 decays at 4 locations around the receiving room for a total of 16 measurements, per ASTM E2235-04(2012).
TEST INSTRUMENTATION:
Equipment Type | Manufacturer | Model Number | Serial Number |  | Last NIST Traceable Calibration | Last Local Calibration
Tapping Machine: | Norsonics | CAL200 | 2775671 |  | 2022-09-19 | N/A
Sound Level Meter | Larson Davis | 831 | 4328 |  | 2022-10-24 | 2024-04-04
Microphone Pre-Amp | Larson Davis | PRM831 | 046469 |  | 2022-10-24 | 2024-04-04
Microphone | Larson Davis | 377B20 | 168830 |  | 2022-10-20 | 2024-04-04
Calibrator | Larson Davis | CAL200 | 5955 |  | 2022-10-26 | N/A
Amplified Loudspeaker | QSC | K10 | GAA530909 |  | N/A | N/A
Noise Generator | NTi Audio | MR-PRO | 0162 |  | N/A | N/A
STATEMENT OF TEST RESULTS:
Frequency | Absorption Normalized Impact Sound Pressure Level, ANISPL (dB) |  | Average Receiver Background Level | Average RT60 (Seconds) | Exceptions noted to ASTM E1007-14
100 | 82 |  | 35.4 | 0.61783
125 | 83 |  | 39.2 | 0.84579
160 | 79 |  | 33 | 0.63261
200 | 76 |  | 37.1 | 0.99566
250 | 77 |  | 34.4 | 1.0232
315 | 74 |  | 33.7 | 1.1372
400 | 69 |  | 33.3 | 1.3446
500 | 63 |  | 32.5 | 1.2621
630 | 56 |  | 31.2 | 1.1412
800 | 50 |  | 30.6 | 1.1179
1000 | 46 |  | 29.6 | 1.2872
1250 | 47 |  | 28.9 | 1.4592
1600 | 45 |  | 28.5 | 1.5181
2000 | 45 |  | 24.9 | 1.4609
2500 | 41 |  | 20.6 | 1.3927
3150 | 38 |  | 18.5 | 1.4027
4000 | 34 |  | 17.6 | 1.3876
5000 | 31 |  | 15.1 | 1.3159
[5 empty] | 0 | 0 | 0
AIIC: 38
An Apparent Impact Insulation Class (AIIC) of 38 and an Impact Sound Rating (ISR) of 42 was calculated. The AIIC rating is based on Absorption Normalized Impact Sound Pressure Level (ANISPL), and includes the effects of noise flanking. The AIIC reference contour is shown on the next page, and has been “fit” to the ANISPL values, in accordance with the procedure of ASTM E989-06(2012). | [7 empty] | An Apparent Impact Insulation Class (AIIC) of 38 and an Impact Sound Rating (ISR) of 42 was calculated. The AIIC rating is based on Absorption Normalized Impact Sound Pressure Level (ANISPL), and includes the effects of noise flanking. The AIIC reference contour is shown on the next page, and has been “fit” to the ANISPL values, in accordance with the procedure of ASTM E989-06(2012).
The results stated in this report represent only the specific construction and acoustical conditions present at the time of the test. Measurements performed in accordance with this test method on nominally identical constructions and acoustical conditions may produce different results. | [7 empty] | The results stated in this report represent only the specific construction and acoustical conditions present at the time of the test. Measurements performed in accordance with this test method on nominally identical constructions and acoustical conditions may produce different results.
AIIC: 38
Test Conducted By:
Zane Wright, Project Consultant |  |  |  |  | Jake Pfitsch, Project Consultant

## ISR Report
Frequency (Hz)
Report Date: | 2024-04-18 |  | Source Room: |  | 2nd Floor Kitchen, Volume: 3950 cu. ft. |  |  |  |  | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000
Test Date: | 2024-04-04 |  | Receiver Room: |  | 1st Floor Great Room/Kitchen, Volume: 3950 cu. ft. |  |  |  | Avg. Source Room Sound Pressure (dB) | 95.8 | 95 | 91.4 | 90 | 91.6 | 89.7 | 88.8 | 84.7 | 82.5 | 84.5 | 83 | 83.8 | 81.4 | 79.8 | 82.4 | 84 | 85 | 84.3
DLAA Test No: | 1.2.1 |  | Test Assembly: |  | Floor-ceiling, Area: 428 sq. ft. |  |  |  | Pink Noise Receiver Room | 78.2 | 79.5 | 73 | 65.6 | 61.6 | 57.6 | 52.7 | 47.5 | 42 | 40.4 | 35.1 | 32.4 | 30.2 | 27.5 | 24.1 | 21.6 | 19.7 | 18.1
[9 empty] | Receiver B.G. | 35.4 | 39.2 | 33 | 37.1 | 34.4 | 33.7 | 33.3 | 32.5 | 31.2 | 30.6 | 29.6 | 28.9 | 28.5 | 24.9 | 20.6 | 18.5 | 17.6 | 15.1
Test Site: | Ka'ulu by Gentry | [7 empty] | RT60 Average | 0.61783 | 0.84579 | 0.63261 | 0.99566 | 1.0232 | 1.1372 | 1.3446 | 1.2621 | 1.1412 | 1.1179 | 1.2872 | 1.4592 | 1.5181 | 1.4609 | 1.3927 | 1.4027 | 1.3876 | 1.3159
Client: | Gentry Builders, LLC
STANDARDS
ASTM E1007-14 | Standard Test Method for Field Measurement of Tapping Machine Impact Sound Transmission Through Floor-Ceiling Assemblies and Associated Support Structure | [6 empty] | Standard Test Method for Field Measurement of Tapping Machine Impact Sound Transmission Through Floor-Ceiling Assemblies and Associated Support Structure
ASTM E989-06(2012) | Standard Classification for Determination of Impact Insulation Class (IIC) | [6 empty] | ASTM E989-06(2012)
ASTM E2235-04(2012) | Standard Test Method for Determination of Decay Rates for Use in Sound Insulation Test Methods | [6 empty] | ASTM E2235-04(2012)
STATEMENT OF CONFORMANCE:
Testing was conducted in general accordance with ASTM E1007-14, with all exceptions noted below. The requirements for measuring and reporting Absorption Normalized Impact Sound Pressure Levels (ANISPL) and Apparent Impact Insulation Class (AIIC) were not met, therefore only Impact Sound Pressure Level (ISPL) and Impact Sound Rating (ISR) have been reported. Exceptions to ASTM E1007-14 that disallow reporting ANISPL and AIIC are as follows: | [7 empty] | Testing was conducted in general accordance with ASTM E1007-14, with all exceptions noted below. The requirements for measuring and reporting Absorption Normalized Impact Sound Pressure Levels (ANISPL) and Apparent Impact Insulation Class (AIIC) were not met, therefore only Impact Sound Pressure Level (ISPL) and Impact Sound Rating (ISR) have been reported. Exceptions to ASTM E1007-14 that disallow reporting ANISPL and AIIC are as follows:
The receiver room had a volume less than the minimum volume requirement of 40 m3. | [7 empty] | The receiver room had a volume less than the minimum volume requirement of 40 m3.
TEST ENVIRONMENT:
The source room was 2nd Floor Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The source room had a volume of approximately 3949 cu. ft. | [7 empty] | The source room was 2nd Floor Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The source room had a volume of approximately 3949 cu. ft.
The receiver room was 1st Floor Great Room/Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The receiver room had a volume of approximately 3950 cu. ft. | [7 empty] | The receiver room was 1st Floor Great Room/Kitchen. The space was finished unfurnished. The floor was LVT. The ceiling was gyp. The walls were gyp. All doors and windows were closed during the testing period. The receiver room had a volume of approximately 3950 cu. ft.
The test assembly measured approximately 14.8x29.583, and had an approximate area of 428 sq. ft. | [7 empty] | The test assembly measured approximately 14.8x29.583, and had an approximate area of 428 sq. ft.
TEST ASSEMBLY:
The tested assembly was the Floor-ceiling The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations. | [7 empty] | The tested assembly was the Floor-ceiling The assembly was not field verified, and was based on information provided by the client and drawings for the project. The client advised that no slab treatment or self-leveling was applied. Results may vary if slab treatment or self-leveling or any adhesive is used in other installations.
TEST PROCEDURE:
The test was performaned in general accordance with ASTM E1007-14. Determination of Space-Average Levels performed via the manually scanned microphones techique, described in ASTM E1007-14, Paragraph 11.4.2.2. | [7 empty] | The test was performaned in general accordance with ASTM E1007-14. Determination of Space-Average Levels performed via the manually scanned microphones techique, described in ASTM E1007-14, Paragraph 11.4.2.2.
Flanking transmission was not evaluated.
To evaluate room absorption, 1 microphone was used to measure 4 decays at 4 locations around the receiving room for a total of 16 measurements, per ASTM E2235-04(2012). | [7 empty] | To evaluate room absorption, 1 microphone was used to measure 4 decays at 4 locations around the receiving room for a total of 16 measurements, per ASTM E2235-04(2012).
TEST INSTRUMENTATION:
Equipment Type | Manufacturer | Model Number | Serial Number |  | Last NIST Traceable Calibration | Last Local Calibration
Tapping Machine: | Norsonics | #REF! | #REF! |  | #REF! | 2024-04-04
Sound Level Meter | Larson Davis | 831 | 3784 |  | 2022-09-19 | 2024-04-04
Microphone Pre-Amp | Larson Davis | PRM831 | 051188 |  | 2022-09-19 | 2024-04-04
Microphone | Larson Davis | 377B20 | 301698 |  | 2022-09-16 | 2024-04-04
Calibrator: | Larson Davis | CAL200 | #REF! |  | #REF! | N/A
Amplified Loudspeakers (QTY 2) | QSC | K10 | GAA530909 |  | N/A | N/A
Noise Generator: | NTi Audio | MR-PRO | 0162 |  | N/A | N/A
STATEMENT OF TEST RESULTS:
Frequency | Impact Sound Pressure Level, ISPL (dB) |  | Average Receiver Background Level | Average RT60 (Seconds) | Exceptions noted to ASTM E1007-14
100 | 77.134 |  | 35.4 | 0.61783
125 | 79.2538 |  | 39.2 | 0.84579
160 | 74.4402 |  | 33 | 0.63261
200 | 73.2975 |  | 37.1 | 0.99566
250 | 74.3392 |  | 34.4 | 1.0232
315 | 71.611 |  | 33.7 | 1.1372
400 | 67.6428 |  | 33.3 | 1.3446
500 | 61.7255 |  | 32.5 | 1.2621
630 | 54.3417 |  | 31.2 | 1.1412
800 | 48.3812 |  | 30.6 | 1.1179
1000 | 44.3479 |  | 29.6 | 1.2872
1250 | 45.9783 |  | 28.9 | 1.4592
1600 | 43.8788 |  | 28.5 | 1.5181
2000 | 44.3888 |  | 24.9 | 1.4609
2500 | 39.6455 |  | 20.6 | 1.3927
3150 | 36.4536 |  | 18.5 | 1.4027
4000 | 32.5693 |  | 17.6 | 1.3876
5000 | 29.757 |  | 15.1 | 1.3159
[5 empty] | 0 | 0 | 0
ISR: 42
A Impact Sound Rating (ISR) of 42 was calculated. The ISR rating is based on Impact Sound Pressure Level (ISPL), and includes the effects of noise flanking. The ISR reference contour is shown on the next page, and has been “fit” to the ISPL values, in accordance with the procedure of ASTM E989-06(2012). | [7 empty] | A Impact Sound Rating (ISR) of 42 was calculated. The ISR rating is based on Impact Sound Pressure Level (ISPL), and includes the effects of noise flanking. The ISR reference contour is shown on the next page, and has been “fit” to the ISPL values, in accordance with the procedure of ASTM E989-06(2012).
The results stated in this report represent only the specific construction and acoustical conditions present at the time of the test. Measurements performed in accordance with this test method on nominally identical constructions and acoustical conditions may produce different results. | [7 empty] | The results stated in this report represent only the specific construction and acoustical conditions present at the time of the test. Measurements performed in accordance with this test method on nominally identical constructions and acoustical conditions may produce different results.
ISR: 39
Test Conducted By:
Zane Wright, Project Consultant |  |  |  |  | Jake Pfitsch, Project Consultant

## ASTC Test Form
ASTC Test Form | [7 empty] | DLAA
Project Name: | [5 empty] | Source Room:
Project Number: | [5 empty] | Receiving Room:
Test Date: | [5 empty] | Partition:
Test Number: | [5 empty] | Conducted By:
Measurement Run Numbers:
Source Pink Noise
Receiver Pink Noise
Receiver Background
RT-60
Notes and Sketches:
Source Room: Floor / Ceiling / Wall Finishes:
Receiver Room: Floor / Ceiling / Wall Finishes:
Source + Receiver Room Dimensions
5300 ft3 max for ASTC (except for very low absorption rooms)
883 ft3 min for ASTC
7.5' min. dimensions for ASTC
| Source Room |  |  | Receiver Room
|  | Add speaker here | 33% Opening Min. |  | 33% Opening Min.
|  | +/- 3 dB | +/- 6 dB |  | +/- 6 dB |  | Ignore corridors narrower than 39" wide (3'-3")
from measurements and volume calcs

## AIIC Test Form
AIIC Test Form | [7 empty] | DLAA
Project Name: | [5 empty] | Source Room:
Project Number: | [5 empty] | Receiving Room:
Test Date: | [5 empty] | Partition:
Test Number: | [5 empty] | Conducted By:
Measurement Run Numbers:
Source Pink Noise |  |  |  |  | Receiver Position #1 |  | Receiver Position #2
Receiver Pink Noise |  |  |  |  | Receiver Position #3 |  | Receiver Position #4
Receiver Background |  |  |  |  | Receiver w. Carpet
RT-60 |  |  |  |  | Source Room Tapper
Notes and Sketches:
Source Room: Floor / Ceiling / Wall Finishes:
Receiver Room: Floor / Ceiling / Wall Finishes:
Source + Receiver Room Dimensions
5300 ft3 max for AIIC (except for very low absorption rooms)
1413 ft3 min for AIIC
Source Room
|  |  | 33% Opening | Ignore corridors narrower than 39" wide (3'-3")
| Receiver Room |  | +/- 6 dB | from measurements and volume calcs

## ASTC Source
| 1/1 Octave | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28 | Unnamed: 29 | Unnamed: 30 | Unnamed: 31 | Unnamed: 32 | Unnamed: 33 | Unnamed: 34 | Unnamed: 35 | Unnamed: 36
0 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
1 | Overall 1/1 Spectra | 64.1 | 58.5 | 74.5 | 101.3 | 99.5 | 95.3 | 90.9 | 88.6 | 86.1 | 89.2 | 89.1 | 85.4
2 | Max 1/1 Spectra | 74.7 | 69 | 81.5 | 106.2 | 104 | 97.7 | 94.7 | 91.8 | 87.5 | 91.3 | 91.5 | 89.3
3 | Min 1/1 Spectra | 55.5 | 48.4 | 64.4 | 93.1 | 93.9 | 92.4 | 87.7 | 85.4 | 84 | 87.3 | 87 | 82.4
4
5 | 1/3 Octave
6 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
7 | Overall 1/3 Spectra | 59.8 | 56.8 | 52.9 | 47.7 | 56.7 | 52.7 | 51.4 | 54.1 | 74.1 | 85.1 | 93.3 | 100.5 | 95.8 | 95 | 91.4 | 90 | 91.6 | 89.7 | 88.8 | 84.7 | 82.5 | 84.5 | 83 | 83.8 | 81.4 | 79.8 | 82.4 | 84 | 85 | 84.3 | 84.1 | 84.2 | 84.6 | 82.8 | 80.7 | 74.9
8 | Max 1/3 Spectra | 65.9 | 67.7 | 62.4 | 54.4 | 68.5 | 57.9 | 57.9 | 60.9 | 81.2 | 92.3 | 100.9 | 105.9 | 101.9 | 99.9 | 97.1 | 93.6 | 94.3 | 92.9 | 92.6 | 88.8 | 86.6 | 89.1 | 86.6 | 87.2 | 83.7 | 81.8 | 84.4 | 85.9 | 86.7 | 86.9 | 86.3 | 86.8 | 87 | 86.1 | 85.1 | 81.7
9 | Min 1/3 Spectra | 52 | 48.6 | 45.5 | 38.6 | 39.8 | 43 | 40.9 | 46.4 | 63 | 70.5 | 84.9 | 92.4 | 91.3 | 85.8 | 83 | 85.1 | 87.7 | 87.1 | 84.4 | 80.1 | 78.8 | 81.3 | 78.8 | 80.6 | 79.1 | 77.5 | 80.2 | 82.5 | 82.7 | 82.5 | 82.3 | 81.9 | 82.4 | 80.2 | 77.2 | 69.1
10
11 | L(20-200Hz) | 103.6272
12
13 | LZS1.00 | 65.2 | 62.5 | 61.4 | 53.9 | 67.1 | 57.5 | 56.4 | 60.1 | 80.6 | 91.6 | 100.3 | 105.3 | 101.6 | 99.3 | 96.2 | 93.3 | 93.9 | 92.5 | 92 | 88.4 | 86.2 | 88.5 | 86.4 | 86.9 | 83.5 | 81.6 | 84.2 | 85.5 | 86.6 | 86.7 | 86.2 | 86.6 | 86.9 | 85.9 | 84.9 | 81.2
14 | LZS10.00 | 62.8 | 58.5 | 55 | 50.4 | 60.9 | 55.4 | 54.2 | 57.6 | 77.9 | 88.3 | 95.9 | 103.4 | 98.2 | 97.9 | 94.6 | 92.1 | 92.8 | 91 | 90.9 | 86.7 | 83.9 | 86.5 | 85.6 | 85.6 | 82.4 | 80.9 | 83.6 | 84.9 | 85.9 | 85.8 | 85.5 | 85.8 | 86.2 | 85.1 | 83.8 | 79.6
15 | LZS33.30 | 60.3 | 56.4 | 52.3 | 47.4 | 53 | 53.2 | 52.1 | 54.1 | 74.9 | 85.5 | 93.2 | 101 | 95.7 | 96 | 92 | 90.5 | 92 | 90 | 89.2 | 84.9 | 82.9 | 84.9 | 83.4 | 84.3 | 81.9 | 80 | 82.7 | 84.3 | 85.2 | 84.3 | 84.4 | 84.4 | 85.1 | 83.1 | 80.8 | 74.3
16 | LZS50.00 | 58.2 | 55.4 | 51 | 45.8 | 51.1 | 52.3 | 50.7 | 52.3 | 72 | 84 | 92.3 | 99.6 | 94.7 | 94.6 | 90.9 | 89.7 | 91.6 | 89.6 | 88.4 | 84.2 | 82.3 | 84.2 | 82.7 | 83.4 | 81.3 | 79.7 | 82.4 | 84.1 | 84.9 | 84 | 84 | 84 | 84.3 | 82.3 | 79.5 | 72.4
17 | LZS66.60 | 57 | 54 | 49.8 | 44.6 | 49.5 | 50.7 | 49.6 | 51.2 | 70.6 | 82.3 | 91.1 | 98.5 | 93.9 | 92.2 | 89.5 | 88.8 | 91 | 89.1 | 87.3 | 83.6 | 81.9 | 83.2 | 81.6 | 82.8 | 80.8 | 79.5 | 82.1 | 83.6 | 84.6 | 83.8 | 83.6 | 83.4 | 83.8 | 81.6 | 78.7 | 71.3
18 | LZS90.00 | 54.4 | 50.7 | 48.1 | 42.8 | 44 | 47.8 | 44.7 | 49.3 | 65.8 | 75.3 | 87.3 | 95.4 | 92.7 | 89.6 | 87 | 87 | 89.7 | 88.1 | 86 | 82.3 | 80.7 | 82 | 80.2 | 82.1 | 80 | 78.8 | 81.4 | 83 | 84.1 | 83.3 | 82.9 | 82.8 | 83.1 | 80.7 | 77.7 | 70.1
19
20
21 | 1/1 OBA Ref. Spectra
22 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27
28 | 1/3 OBA Ref. Spectra
29 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34
35
36 | 1/1 OBA Under Range
37 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
38 | Under Range Limit | 62.7 | 55.8 | 53.8 | 48.8 | 45.8 | 46.8 | 50.8 | 45.9 | 48.9 | 50.8 | 52.8 | 55.8
39 | Noise Floor | 32.7 | 32.7 | 31.2 | 30.3 | 31.9 | 31.9 | 34.3 | 32.6 | 34.5 | 37.6 | 41.1 | 44.4
40
41 | 1/3 OBA Under Range
42 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
43 | Under Range Limit | 52.8 | 49.8 | 48.8 | 49.8 | 49.8 | 48.8 | 46.8 | 47.8 | 47.8 | 45.8 | 43.8 | 42.8 | 43.8 | 44.8 | 40.8 | 41.8 | 41.8 | 39.8 | 43.8 | 42.8 | 39.9 | 40.9 | 43.8 | 41.8 | 40.8 | 40.8 | 41.8 | 44.8 | 43.9 | 45.9 | 47.8 | 49.8 | 48.9 | 49.9 | 50.8 | 52.8
44 | Noise Floor | 28.4 | 27.5 | 29.2 | 29 | 26.3 | 28.5 | 26.5 | 27.3 | 26.5 | 26 | 26.5 | 26.6 | 25.8 | 25.4 | 26 | 26.4 | 28.5 | 27.3 | 26.8 | 26.7 | 26.7 | 27.4 | 27.8 | 28.7 | 29.2 | 29.7 | 30.7 | 31.8 | 32.8 | 34 | 34.7 | 36.3 | 37.4 | 38.4 | 39.4 | 41

## ASTC Receive
| 1/1 Octave | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28 | Unnamed: 29 | Unnamed: 30 | Unnamed: 31 | Unnamed: 32 | Unnamed: 33 | Unnamed: 34 | Unnamed: 35 | Unnamed: 36
0 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
1 | Overall 1/1 Spectra | 55.2 | 55.6 | 55 | 81.2 | 82.6 | 67.6 | 54.3 | 42 | 32.7 | 24.9 | 20.4 | 16.7
2 | Max 1/1 Spectra | 60.6 | 59.7 | 59.5 | 86.2 | 87.8 | 70.6 | 55.8 | 45.1 | 35.4 | 29.5 | 25 | 18.2
3 | Min 1/1 Spectra | 50.4 | 49.6 | 49.7 | 75.2 | 75.5 | 63.7 | 52.6 | 40.8 | 31.2 | 22.9 | 17.8 | 15.6
4
5 | 1/3 Octave
6 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
7 | Overall 1/3 Spectra | 52.3 | 50.5 | 48 | 49.5 | 53.1 | 49 | 47.7 | 44 | 53.6 | 62.1 | 76.1 | 79.6 | 78.2 | 79.5 | 73 | 65.6 | 61.6 | 57.6 | 52.7 | 47.5 | 42 | 40.4 | 35.1 | 32.4 | 30.2 | 27.5 | 24.1 | 21.6 | 19.7 | 18.1 | 16.9 | 15.7 | 13.9 | 12.3 | 11.6 | 11.8
8 | Max 1/3 Spectra | 57.8 | 59 | 53.9 | 56.5 | 58.8 | 53.9 | 54.2 | 55.6 | 58.9 | 67.8 | 81.9 | 85.2 | 86.9 | 85.4 | 77.4 | 69.4 | 63.8 | 60.4 | 55 | 49.6 | 43.9 | 44.5 | 37.6 | 36.9 | 35 | 30.1 | 30.8 | 26.8 | 23.5 | 22.8 | 22.3 | 21.3 | 18 | 14.6 | 12.7 | 12.8
9 | Min 1/3 Spectra | 46.1 | 44.4 | 42.1 | 42.9 | 44.7 | 42.4 | 39.4 | 34.6 | 42.4 | 53.9 | 67.7 | 73.6 | 69.9 | 72.1 | 66.7 | 59.1 | 57.7 | 53.7 | 51.1 | 45.4 | 39.9 | 39 | 33.6 | 31.1 | 28.5 | 26 | 22.7 | 20 | 17.9 | 15.3 | 13.2 | 13 | 10.7 | 10.5 | 10.6 | 11.4
10
11 | L(20-200Hz) | 84.9517
12
13
14 | 1/1 OBA Ref. Spectra
15 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20
21 | 1/3 OBA Ref. Spectra
22 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27
28
29 | 1/1 OBA Under Range
30 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
31 | Under Range Limit | 33.9 | 30.7 | 28.9 | 27.9 | 24.9 | 18.9 | 16.9 | 20.9 | 18.9 | 21 | 22.7 | 24.9
32 | Noise Floor | 16.1 | 14.8 | 10.8 | 8.3 | 6.9 | 5.8 | 6.7 | 8 | 9.7 | 11.9 | 13.5 | 14.8
33
34 | 1/3 OBA Under Range
35 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
36 | Under Range Limit | 37.9 | 34.9 | 30.9 | 33.5 | 32.7 | 30.7 | 27.9 | 23.9 | 23.9 | 22.9 | 21.9 | 25.9 | 24.9 | 21.9 | 20.9 | 21.9 | 15.9 | 12.9 | 13.9 | 19.9 | 12.9 | 14.9 | 13.9 | 12.8 | 13.3 | 14.2 | 14.9 | 15.7 | 16.3 | 16.9 | 17.5 | 17.9 | 18.9 | 19.9 | 19.9 | 21.7
37 | Noise Floor | 14.3 | 11.6 | 10.3 | 10.8 | 8.9 | 8 | 7.5 | 7.3 | 5.6 | 3.6 | 3.6 | 3.4 | 2.8 | 1.2 | 1.1 | 1.3 | 0.7 | 1.3 | 2 | 2.2 | 2.4 | 2.6 | 3 | 3.6 | 4.2 | 5.1 | 5.7 | 6.5 | 7.1 | 7.8 | 8.3 | 8.8 | 9.1 | 9.7 | 9.9 | 10.9

## BNL
| 1/1 Octave | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28 | Unnamed: 29 | Unnamed: 30 | Unnamed: 31 | Unnamed: 32 | Unnamed: 33 | Unnamed: 34 | Unnamed: 35 | Unnamed: 36
0 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
1 | Overall 1/1 Spectra | 53 | 57.5 | 52.7 | 48 | 41.4 | 40.1 | 37.2 | 34.5 | 30.6 | 22 | 16.1 | 15.1
2 | Max 1/1 Spectra | 63 | 64 | 59.2 | 53.1 | 47.9 | 47.5 | 45.2 | 42.1 | 34.8 | 29.3 | 26 | 21.1
3 | Min 1/1 Spectra | 46.8 | 52.4 | 48.4 | 41.7 | 36.2 | 34.5 | 28.5 | 29.5 | 25.7 | 18.7 | 15.1 | 14.9
4
5 | 1/3 Octave
6 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
7 | Overall 1/3 Spectra | 50 | 48.7 | 47.2 | 48.6 | 53.6 | 54.5 | 50.2 | 44.6 | 46.7 | 46.8 | 38.9 | 38.6 | 35.4 | 39.2 | 33 | 37.1 | 34.4 | 33.7 | 33.3 | 32.5 | 31.2 | 30.6 | 29.6 | 28.9 | 28.5 | 24.9 | 20.6 | 18.5 | 17.6 | 15.1 | 12.3 | 11.1 | 10.4 | 10.1 | 10.1 | 10.9
8 | Max 1/3 Spectra | 69.4 | 63.9 | 56.8 | 56 | 60 | 61.2 | 58.7 | 48.8 | 50.9 | 52.9 | 44.4 | 44.9 | 42.1 | 47.1 | 40.5 | 43.8 | 44.7 | 39.5 | 40.7 | 41.7 | 40.6 | 40.7 | 34.8 | 33.9 | 32.3 | 29.6 | 26.4 | 25 | 25 | 23.9 | 22.5 | 21.2 | 19.5 | 18.4 | 15.8 | 13.2
9 | Min 1/3 Spectra | 39.6 | 39.6 | 38.4 | 40.2 | 45.2 | 48.5 | 45.3 | 40.6 | 41 | 37.9 | 32.5 | 32.8 | 30.6 | 31.6 | 27.4 | 31.5 | 26.9 | 27.4 | 23.3 | 23 | 23.2 | 24.9 | 24.4 | 23.7 | 23.6 | 20 | 16.5 | 14.4 | 14.1 | 12.1 | 10.8 | 10.1 | 9.7 | 9.8 | 9.9 | 10.7
10
11 | L(20-200Hz) | 57.3555
12
13
14 | 1/1 OBA Ref. Spectra
15 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20
21 | 1/3 OBA Ref. Spectra
22 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27
28
29 | 1/1 OBA Under Range
30 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
31 | Under Range Limit | 33.9 | 30.7 | 28.9 | 27.9 | 24.9 | 18.9 | 16.9 | 20.9 | 18.9 | 21 | 22.7 | 24.9
32 | Noise Floor | 16.1 | 14.8 | 10.8 | 8.3 | 6.9 | 5.8 | 6.7 | 8 | 9.7 | 11.9 | 13.5 | 14.8
33
34 | 1/3 OBA Under Range
35 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
36 | Under Range Limit | 37.9 | 34.9 | 30.9 | 33.5 | 32.7 | 30.7 | 27.9 | 23.9 | 23.9 | 22.9 | 21.9 | 25.9 | 24.9 | 21.9 | 20.9 | 21.9 | 15.9 | 12.9 | 13.9 | 19.9 | 12.9 | 14.9 | 13.9 | 12.8 | 13.3 | 14.2 | 14.9 | 15.7 | 16.3 | 16.9 | 17.5 | 17.9 | 18.9 | 19.9 | 19.9 | 21.7
37 | Noise Floor | 14.3 | 11.6 | 10.3 | 10.8 | 8.9 | 8 | 7.5 | 7.3 | 5.6 | 3.6 | 3.6 | 3.4 | 2.8 | 1.2 | 1.1 | 1.3 | 0.7 | 1.3 | 2 | 2.2 | 2.4 | 2.6 | 3 | 3.6 | 4.2 | 5.1 | 5.7 | 6.5 | 7.1 | 7.8 | 8.3 | 8.8 | 9.1 | 9.7 | 9.9 | 10.9

## RT
| Unnamed: 0 | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28 | Unnamed: 29 | Unnamed: 30 | Unnamed: 31 | Unnamed: 32 | Unnamed: 33 | Unnamed: 34 | Unnamed: 35 | Unnamed: 36 | Unnamed: 37 | Unnamed: 38 | Unnamed: 39
0 | Summary
1 | File Name | RT_Data.140.r
2 | Serial Number | 4328
3 | Model | Model 831
4 | Firmware Version | 2.403
5 | User
6 | Location
7 | Job Description
8 | Note
9 | Measurement Description | RT60
10 | Start | 2024-04-04 16:04
11 | Stop | 2024-04-04 16:08
12 | Duration | 00:03:23.100000
13 | Run Time | 00:03:23.100000
14 | Pause | 00:00:00
15
16 | Pre-Calibration | 2024-04-04 13:54
17 | Post-Calibration
18 | Calibration Deviation | ---
19
20 | Ensemble | 16
21 | Frequency (Hz) | Leq (dB) | Lmax (dB) | Lbk (dB) | T20 (ms) | BT:T20 | BK:T20 (dB SNR) | NL:T20 (‰) | Cu:T20 (%) | Sd:T20 (%) | T30 (ms) | BT:T30 | BK:T30 (dB SNR) | NL:T30 (‰) | Cu:T30 (%) | Sd:T30 (%)
22 | 63.0 Hz | 92.7029 | 94.9406 | 49.0763 | 837.2316 | 12.1901 | 43.6266 | 12.2541 | 8.7896 | 15.3054 | 910.8209 | 13.2615 | 43.6266 | 11.1458 | 8.7896 | 8.8711
23 | 80.0 Hz | 98.4807 | 101.0305 | 49.5845 | 706.4796 | 12.9498 | 48.8962 | 23.9587 | 2.3731 | 14.8497 | 723.2454 | 13.2571 | 48.8962 | 9.7295 | 2.3731 | 8.8725
24 | 100 Hz | 91.6288 | 94.5944 | 46.2592 | 623.4726 | 14.3897 | 45.3696 | 18.0189 | -0.90544 | 14.0871 | 617.8274 | 14.2595 | 45.3696 | 8.3869 | -0.90544 | 8.555
25 | 125 Hz | 93.6358 | 96.8534 | 43.1969 | 803.2314 | 23.3339 | 50.439 | 13.2661 | 5.2982 | 11.0625 | 845.7884 | 24.5702 | 50.439 | 6.3253 | 5.2982 | 6.5173
26 | 160 Hz | 88.9304 | 91.4621 | 42.5438 | 689.3645 | 25.2101 | 46.3866 | 43.9876 | -8.2328 | 10.6429 | 632.6104 | 23.1346 | 46.3866 | 16.4086 | -8.2328 | 6.7165
27 | 200 Hz | 88.9125 | 91.2894 | 46.949 | 986.6089 | 45.4235 | 41.9635 | 43.0818 | 0.91695 | 7.9288 | 995.6555 | 45.84 | 41.9635 | 30.1443 | 0.91695 | 4.7714
28 | 250 Hz | 91.1607 | 94.2769 | 39.5064 | 993.4716 | 57.5915 | 51.6543 | 49.9994 | 2.9933 | 7.0416 | 1023.209 | 59.3154 | 51.6543 | 25.1041 | 2.9933 | 4.1946
29 | 315 Hz | 92.1612 | 94.461 | 37.1869 | 1098.708 | 80.1837 | 54.9743 | 23.0877 | 3.5036 | 5.9677 | 1137.202 | 82.993 | 54.9743 | 11.8046 | 3.5036 | 3.5461
30 | 400 Hz | 92.0894 | 95.0829 | 35.416 | 1239.876 | 113.9075 | 56.6734 | 62.4409 | 8.4483 | 5.0069 | 1344.625 | 123.5307 | 56.6734 | 22.5031 | 8.4483 | 2.9066
31 | 500 Hz | 89.9621 | 93.1076 | 35.4401 | 1200.354 | 138.8329 | 54.522 | 42.2879 | 5.1448 | 4.5353 | 1262.11 | 145.9756 | 54.522 | 15.7648 | 5.1448 | 2.6738
32 | 630 Hz | 88.5922 | 92.6519 | 36.0107 | 1086.377 | 158.1765 | 52.5815 | 24.35 | 5.045 | 4.2489 | 1141.185 | 166.1566 | 52.5815 | 13.7188 | 5.045 | 2.5062
33 | 800 Hz | 89.78 | 92.7114 | 38.0402 | 1113.225 | 204.0652 | 51.7398 | 20.8719 | 0.41778 | 3.7408 | 1117.875 | 204.9177 | 51.7398 | 10.7172 | 0.41778 | 2.2567
34 | 1000 Hz | 88.4571 | 91.336 | 39.272 | 1251.658 | 288.8451 | 49.1851 | 22.2835 | 2.8433 | 3.1442 | 1287.246 | 297.0578 | 49.1851 | 10.515 | 2.8433 | 1.8744
35 | 1250 Hz | 87.0744 | 89.6895 | 37.1313 | 1451.545 | 421.7029 | 49.9432 | 16.4919 | 0.52675 | 2.6022 | 1459.191 | 423.9243 | 49.9432 | 8.9496 | 0.52675 | 1.569
36 | 1600 Hz | 83.705 | 86.7241 | 35.3206 | 1537.625 | 562.3709 | 48.3844 | 19.5706 | -1.2681 | 2.2534 | 1518.126 | 555.2394 | 48.3844 | 9.1557 | -1.2681 | 1.371
37 | 2000 Hz | 80.4631 | 82.8156 | 32.3409 | 1418.387 | 653.0822 | 48.1222 | 18.0752 | 2.9982 | 2.0911 | 1460.914 | 672.663 | 48.1222 | 9.7035 | 2.9982 | 1.2456
38 | 2500 Hz | 83.3479 | 85.6389 | 29.2962 | 1390.75 | 806.1624 | 54.0517 | 10.9974 | 0.13813 | 1.8821 | 1392.672 | 807.276 | 54.0517 | 6.2298 | 0.13813 | 1.137
39 | 3150 Hz | 85.3408 | 88.485 | 27.3493 | 1397.51 | 1019.833 | 57.9914 | 10.4993 | 0.37446 | 1.6733 | 1402.743 | 1023.651 | 57.9914 | 4.2391 | 0.37446 | 1.0097
40 | 4000 Hz | 85.8327 | 87.6907 | 27.4184 | 1357.28 | 1246.933 | 58.4143 | 5.5999 | 2.2343 | 1.5133 | 1387.606 | 1274.794 | 58.4143 | 2.9352 | 2.2343 | 0.9048
41 | 5000 Hz | 84.2017 | 85.8287 | 26.3893 | 1299.585 | 1503.074 | 57.8124 | 7.5352 | 1.2526 | 1.3783 | 1315.864 | 1521.902 | 57.8124 | 3.687 | 1.2526 | 0.82809
42 | 6300 Hz | 82.9878 | 84.2909 | 24.7672 | 1169.955 | 1703.501 | 58.2205 | 6.7776 | 0.040221 | 1.2947 | 1170.426 | 1704.187 | 58.2205 | 2.4348 | 0.040221 | 0.78255
43 | 8000 Hz | 81.6676 | 83.4403 | 21.8256 | 968.5901 | 1775.474 | 59.842 | 6.1748 | 1.6545 | 1.2682 | 984.615 | 1804.849 | 59.842 | 2.544 | 1.6545 | 0.76042
44
45 | RT60 Measurement Grade
46 | Estimated Grade | Settings Conflict
47 | Overload Count | 0
48
49 | Details Used to Calculate Grade
50 | Frequency Range |  |  |  | Survey | Engineering | Precision
51 | Actual | 63.0 Hz - 8000 Hz |  | Source-Mic Combo | 2 | 6 | 12
52 | Required | 100 Hz - 5000 Hz |  | Source-Positions | ≥1 | ≥2 | ≥3
53 | Positions Included in Ensemble |  |  | Mic-Positions | ≥2 | ≥2 | ≥3
54 | Actual | 4 |  | Decays per Position | 1 | 2 | 3
55 | Required | 12 |  | Trigger Method | Both | Interrupted | Interrupted
56 | Decays per Position |  |  | Octave | 1/1 | 1/1 or 1/3 | 1/1 or 1/3
57 | Actual | 4 |  | Frequency Range | 250 Hz - 2 kHz | 125 Hz - 4 kHz (1/1) 100 Hz - 5 kHz (1 / 3)
58 | Required | 1
59
60 | Total Positions Measured | 4
61 | Position | 1 | 2 | 3 | 4
62 | Decays | 4 | 4 | 4 | 4
63
64 | OBA Overload Count | 0
65
66 | Overall Settings
67 | Trigger Method | Interrupted
68 | Trigger Source | Mid Band
69 | Trigger Level | 85 | dB
70 | Noise Source | Pink
71 | Sample Period | 5 | ms
72 | Decay Count | 16
73 | Decays used in ensemble | 16
74
75 | OBA Range | Normal
76 | OBA Bandwidth | 1/3 Octave
77 | Gain | 20 | dB
78
79 |  | First | Second | Third
80 | Instrument Identification
81
82
83 | 1/3 OBA Under Range
84 | Frequency (Hz) | 6.3 | 8.0 | 10.0 | 12.5 | 16.0 | 20.0 | 25.0 | 31.5 | 40.0 | 50.0 | 63.0 | 80.0 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
85 | Under Range Limit | 40.9 | 34.9 | 34.9 | 32.9 | 33.9 | 31.9 | 34.9 | 31.9 | 29.9 | 29.9 | 26.9 | 28.9 | 25.9 | 27.9 | 26.9 | 22.9 | 23.9 | 22.9 | 25.9 | 29.9 | 21.9 | 22.9 | 21.9 | 21.9 | 21.9 | 21.9 | 22.9 | 23.9 | 24.9 | 25.9 | 27.9 | 29.9 | 28.9 | 30.9 | 30.9 | 32.9
86 | Noise Floor | 15.5 | 14.7 | 13.3 | 11.1 | 12.6 | 11.8 | 10.8 | 10.4 | 10.1 | 9.7 | 10.4 | 9.5 | 9.6 | 8.3 | 6.6 | 8 | 7.1 | 7.9 | 10.3 | 8 | 8.5 | 8.7 | 9.1 | 10.2 | 10.7 | 11.4 | 12.3 | 13.2 | 14.2 | 15.5 | 16.5 | 17.3 | 18.6 | 19.6 | 20.6 | 22.2
87
88 | Calibration History
89 | Preamp | Date | dB re. 1V/Pa |  | 6.3 | 8.0 | 10.0 | 12.5 | 16.0 | 20.0 | 25.0 | 31.5 | 40.0 | 50.0 | 63.0 | 80.0 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
90 | Direct | 2022-09-07 09:41 | -105.4202 |  | 28.6172 | 20.0013 | 25.1694 | 30.178 | 18.2429 | 24.3823 | 25.0764 | 27.8174 | 20.0512 | 22.8015 | 25.7273 | 24.1192 | 22.4213 | 21.4725 | 20.3533 | 22.4392 | 19.7725 | 22.0663 | 22.8721 | 23.1826 | 23.7417 | 24.8855 | 25.1951 | 26.0689 | 27.0614 | 28.3199 | 29.2895 | 30.3537 | 31.6021 | 32.3793 | 34.018 | 35.1039 | 36.1588 | 37.3106 | 38.1185 | 39.7965
91 | PRM831 | 2024-04-04 13:54 | -27.9705 |  | 64.009 | 56.9542 | 55.9365 | 50.1831 | 58.3613 | 64.0239 | 53.0734 | 46.4378 | 49.6134 | 49.1893 | 40.1962 | 46.8161 | 47.3661 | 50.4292 | 38.1335 | 39.4674 | 43.0832 | 41.5724 | 43.3151 | 40.9658 | 32.993 | 27.3362 | 94.044 | 31.4019 | 29.1151 | 39.4639 | 31.2353 | 39.621 | 33.6241 | 34.362 | 36.0368 | 37.045 | 38.2849 | 39.3706 | 40.4399 | 42.2743
92 | PRM831 | 2024-04-04 13:54 | -27.9628 |  | 48.7189 | 48.0757 | 54.1549 | 51.4935 | 56.2826 | 55.9941 | 50.5507 | 47.5337 | 50.1312 | 55.4351 | 47.3742 | 53.2103 | 44.5948 | 40.8405 | 40.6429 | 43.1787 | 54.6598 | 58.6509 | 66.7568 | 60.8616 | 48.7088 | 38.3049 | 94.2011 | 30.9582 | 29.6979 | 39.76 | 31.5419 | 39.776 | 33.6854 | 35.0526 | 36.061 | 37.1557 | 38.1978 | 39.1478 | 40.3403 | 42.1136
93 | PRM831 | 2024-03-07 14:48 | -28.1214 |  | 121.827 | 128.9325 | 96.0078 | 97.0233 | 93.4914 | 72.2695 | 63.5288 | 53.8409 | 52.4359 | 45.6659 | 40.8525 | 43.6663 | 43.6835 | 46.7964 | 44.0338 | 43.0948 | 40.6603 | 37.5143 | 41.3429 | 39.8984 | 34.6446 | 29.5855 | 94.0027 | 32.6721 | 29.5388 | 35.1876 | 31.7534 | 53.7337 | 33.9253 | 35.0342 | 35.9387 | 37.2698 | 38.7199 | 39.1141 | 40.579 | 42.0338
94 | PRM831 | 2024-03-07 13:23 | -28.0769 |  | 105.9727 | 119.1633 | 91.3641 | 75.0058 | 63.4479 | 60.7361 | 56.9019 | 52.1822 | 50.4345 | 48.397 | 53.5569 | 48.5237 | 43.2337 | 46.913 | 50.8195 | 52.0916 | 45.9603 | 55.3786 | 49.0164 | 49.5907 | 36.2341 | 28.7858 | 93.8794 | 32.4284 | 31.6669 | 34.3975 | 32.8674 | 53.6227 | 33.6459 | 34.988 | 35.683 | 36.9587 | 38.2552 | 38.869 | 40.2073 | 41.9828
95 | PRM831 | 2023-12-19 19:01 | -27.9174 |  | 40.7081 | 41.2908 | 49.1114 | 48.2103 | 39.3687 | 42.2736 | 42.2993 | 40.4588 | 34.2639 | 43.6852 | 42.9365 | 33.1337 | 39.8113 | 35.5807 | 25.9516 | 26.5871 | 27.3358 | 26.8811 | 28.3993 | 26.0407 | 25.4914 | 27.5178 | 94.0152 | 32.0406 | 29.6694 | 36.6884 | 31.5848 | 39.4684 | 33.823 | 34.7218 | 35.509 | 37.1881 | 38.1785 | 39.1788 | 40.545 | 42.1041
96 | PRM831 | 2023-12-19 17:13 | -27.8861 |  | 63.5456 | 62.418 | 57.0422 | 50.4941 | 58.8068 | 59.1273 | 53.8168 | 47.9526 | 46.1475 | 47.0768 | 40.0873 | 30.3394 | 32.6605 | 34.0171 | 30.5133 | 31.6195 | 34.8515 | 33.9614 | 34.1317 | 30.0106 | 26.4752 | 26.7888 | 94.0992 | 31.8969 | 29.3956 | 36.9613 | 31.4363 | 40.075 | 33.5153 | 34.7486 | 35.7532 | 36.9491 | 38.1094 | 39.2051 | 40.0887 | 41.7882
97 | PRM831 | 2023-12-15 20:10 | -27.9359 |  | 39.4559 | 40.3989 | 28.2978 | 36.2358 | 41.2769 | 45.2824 | 63.8923 | 56.4947 | 59.9346 | 52.0168 | 48.4992 | 37.4326 | 36.4286 | 37.4701 | 32.8685 | 31.1186 | 32.6278 | 28.9855 | 30.6275 | 28.5535 | 26.2721 | 27.5863 | 94.1165 | 32.7129 | 29.6369 | 37.1444 | 31.9765 | 39.0039 | 33.577 | 34.883 | 35.8794 | 37.4361 | 38.5533 | 39.2383 | 40.2813 | 42.1169
98 | PRM831 | 2023-12-15 16:52 | -28.0055 |  | 55.0518 | 57.4348 | 52.5528 | 52.4227 | 54.0941 | 48.3315 | 49.6548 | 50.9243 | 46.9317 | 47.5289 | 46.8064 | 46.5138 | 48.9417 | 48.4324 | 48.2535 | 46.1729 | 44.5733 | 47.5015 | 50.4829 | 45.1351 | 31.6498 | 27.0929 | 94.0435 | 32.0329 | 28.9987 | 37.3815 | 31.581 | 40.2023 | 34.0707 | 34.5908 | 35.5279 | 36.5772 | 38.3987 | 39.3048 | 40.3832 | 41.955
99 | PRM831 | 2023-12-14 17:42 | -27.9988 |  | 118.8137 | 112.2468 | 65.5048 | 59.0743 | 45.2521 | 47.5464 | 43.8864 | 44.4987 | 36.635 | 42.4023 | 42.7984 | 47.8326 | 38.3986 | 39.6028 | 34.4494 | 29.4868 | 31.5639 | 36.4499 | 35.1003 | 32.2145 | 26.899 | 27.3158 | 93.9484 | 32.0414 | 29.3678 | 35.6339 | 31.7467 | 40.3609 | 33.6968 | 34.6253 | 35.9737 | 36.7725 | 38.3975 | 39.3747 | 40.1728 | 42.1043
100 | PRM831 | 2023-12-14 16:38 | -27.8993 |  | 88.5091 | 97.5798 | 81.589 | 63.0346 | 56.0959 | 49.9796 | 47.7948 | 46.3593 | 46.3857 | 42.6265 | 46.194 | 42.4919 | 36.6974 | 43.1955 | 34.5966 | 33.6041 | 32.6502 | 30.3633 | 34.9502 | 35.4703 | 27.9617 | 25.9294 | 93.9972 | 31.6468 | 29.0063 | 36.655 | 31.5636 | 40.1433 | 33.7779 | 34.8031 | 35.7607 | 36.9591 | 38.0966 | 39.1956 | 40.3098 | 41.9545
101 | PRM831 | 2023-11-20 14:15 | -27.8461 |  | 81.0081 | 93.8757 | 93.2216 | 75.8922 | 62.6037 | 53.325 | 47.9935 | 53.6342 | 50.0191 | 51.7919 | 53.3321 | 58.5332 | 52.8722 | 62.4771 | 45.8435 | 44.3306 | 39.8951 | 38.5056 | 34.7749 | 31.9359 | 27.584 | 27.3363 | 93.831 | 31.5381 | 29.6186 | 36.4615 | 31.4383 | 39.3755 | 33.247 | 34.2927 | 35.7424 | 36.7242 | 37.7913 | 38.9902 | 40.1891 | 41.5
102 | ICP | 2022-11-08 16:13 | -25.4274 |  | 90.5403 | 74.0307 | 59.0728 | 54.8201 | 52.5607 | 47.9093 | 52.5177 | 56.2156 | 53.7465 | 43.3081 | 39.3411 | 38.2274 | 38.0897 | 52.5752 | 120.0358 | 56.9714 | 29.5432 | 69.3675 | 28.7905 | 66.8081 | 47.2877 | 47.8567 | 45.135 | 42.2626 | 41.6604 | 39.6706 | 38.336 | 35.2763 | 33.5432 | 34.3184 | 35.832 | 40.5688 | 37.0495 | 38.5034 | 41.0777 | 41.5541
103 | ICP | 2022-11-07 13:24 | -25.3851 |  | 68.3387 | 77.6072 | 61.0064 | 61.1148 | 58.1076 | 56.6009 | 47.1604 | 49.0595 | 48.7143 | 42.3034 | 38.8579 | 33.2229 | 39.4465 | 49.9497 | 120.1678 | 56.9852 | 26.859 | 74.6419 | 25.9761 | 67.0616 | 49.2885 | 50.2861 | 53.9021 | 52.3294 | 51.3 | 49.0325 | 49.8892 | 50.4303 | 49.7533 | 48.7128 | 44.3501 | 55.9372 | 41.6633 | 38.7554 | 41.3668 | 41.7681
104 | ICP | 2022-11-02 18:55 | -25.4731 |  | 52.5641 | 57.6285 | 53.0207 | 53.1102 | 46.8292 | 48.3243 | 47.4205 | 51.1534 | 42.9209 | 37.9988 | 34.8473 | 33.7103 | 33.8407 | 50.5721 | 120.0576 | 56.8668 | 27.2727 | 75.9794 | 25.8887 | 65.6401 | 48.2984 | 48.9922 | 43.3247 | 42.8775 | 36.9097 | 34.7022 | 39.0024 | 36.4688 | 33.4202 | 34.4191 | 35.2657 | 39.2855 | 37.0602 | 38.6875 | 41.5103 | 41.5407
105 | ICP | 2022-11-02 18:55 | -25.4477 |  | 71.5046 | 73.1185 | 59.0151 | 53.6377 | 49.3029 | 53.4864 | 60.5028 | 57.3974 | 54.2838 | 47.0014 | 43.2032 | 39.5047 | 34.1503 | 57.1148 | 120.2821 | 58.0024 | 36.3402 | 75.9203 | 34.8469 | 65.6943 | 47.3205 | 49.977 | 43.1542 | 43.7159 | 39.6594 | 59.8353 | 57.5315 | 49.1475 | 39.2239 | 37.6182 | 37.8118 | 44.3707 | 37.8107 | 38.7246 | 41.3462 | 42.1081
106 | ICP | 2022-05-02 19:26 | -25.656 |  | 60.0593 | 59.5362 | 54.4482 | 63.8846 | 62.4826 | 51.9185 | 49.9957 | 49.9967 | 52.3122 | 44.2826 | 40.1324 | 40.1212 | 41.5363 | 60.8891 | 120.087 | 57.9262 | 44.8096 | 78.0313 | 44.734 | 60.8585 | 38.4428 | 50.3547 | 39.3138 | 37.9006 | 37.7445 | 37.2319 | 35.155 | 35.439 | 35.8444 | 36.9704 | 36.6227 | 39.7396 | 38.4064 | 39.5498 | 42.8083 | 42.6105
107 | ICP | 2022-05-02 19:14 | -25.6665 |  | 61.4009 | 63.7242 | 57.9302 | 62.1998 | 57.0811 | 49.7676 | 51.16 | 55.868 | 49.2452 | 43.3818 | 45.8938 | 40.165 | 39.5444 | 52.122 | 120.0791 | 57.0208 | 29.4831 | 75.7666 | 27.0511 | 65.6995 | 36.3813 | 46.7109 | 35.8536 | 33.7032 | 34.3638 | 35.1175 | 33.2522 | 33.0405 | 33.9285 | 35.3623 | 34.9009 | 38.4341 | 37.3996 | 38.7887 | 43.2838 | 41.8682
108 | ICP | 2022-05-02 19:14 | -25.6644 |  | 57.7638 | 64.2118 | 58.929 | 62.8117 | 55.7846 | 53.9471 | 54.7373 | 54.8279 | 46.5389 | 45.3787 | 41.4855 | 30.977 | 29.3831 | 46.5318 | 119.954 | 56.7775 | 27.0603 | 75.8077 | 24.3273 | 65.7421 | 39.5261 | 50.3181 | 35.4434 | 33.6627 | 34.4064 | 33.5357 | 35.2936 | 33.6771 | 33.7269 | 34.9676 | 35.3166 | 38.9401 | 37.2537 | 38.5312 | 43.0744 | 41.7611
109 | ICP | 2022-05-02 11:52 | -25.539 |  | 67.1075 | 54.9044 | 59.4203 | 57.1492 | 57.4627 | 58.171 | 59.1056 | 52.2242 | 54.2029 | 56.0548 | 50.2639 | 45.281 | 42.6506 | 58.4177 | 120.1522 | 57.0295 | 29.2568 | 71.8678 | 28.9113 | 62.7564 | 33.9197 | 49.3206 | 40.5989 | 38.3125 | 32.1546 | 30.8533 | 31.2458 | 32.316 | 33.3549 | 33.6836 | 35.1806 | 38.2053 | 37.0134 | 38.4996 | 40.4907 | 41.9076
110 | ICP | 2022-05-02 11:22 | -25.6044 |  | 75.5251 | 78.0346 | 81.5428 | 69.272 | 69.748 | 53.7333 | 47.6889 | 51.5078 | 52.3227 | 45.6865 | 42.3748 | 36.1313 | 35.7501 | 51.2482 | 120.119 | 57.0392 | 32.3293 | 75.5909 | 28.7211 | 65.1309 | 40.8162 | 54.3591 | 41.3999 | 40.3338 | 38.2295 | 35.9008 | 37.0928 | 33.9379 | 33.558 | 34.5181 | 35.1913 | 38.2526 | 37.1363 | 38.4198 | 41.6838 | 41.8002
111 | ICP | 2022-04-13 14:39 | -25.6388 |  | 53.2396 | 54.6253 | 53.2196 | 58.816 | 64.1249 | 53.1367 | 47.7693 | 48.3659 | 52.0703 | 37.0178 | 34.0573 | 32.123 | 32.8308 | 51.9863 | 120.118 | 57.2002 | 32.4059 | 75.4759 | 35.8386 | 64.1253 | 38.6234 | 49.5483 | 37.7743 | 37.836 | 38.1856 | 37.8071 | 38.0326 | 33.848 | 33.0824 | 33.7515 | 35.5731 | 39.3615 | 37.1676 | 38.4307 | 40.9744 | 41.7436
112 | ICP | 2021-09-17 11:38 | -25.6792 |  | 59.3325 | 63.7679 | 56.1326 | 53.0569 | 52.3029 | 44.1398 | 45.8376 | 49.1693 | 45.4409 | 37.216 | 38.142 | 35.0769 | 28.6605 | 45.8844 | 120.0976 | 56.9921 | 27.9023 | 74.6042 | 27.956 | 65.1011 | 44.6371 | 50.4247 | 38.4864 | 37.8613 | 35.3673 | 33.7999 | 35.543 | 33.7208 | 32.7933 | 34.3817 | 35.3407 | 38.0619 | 37.1294 | 38.3779 | 40.5411 | 41.9007
113 | 426A12 | 2023-11-20 20:49 | -27.8843 |  | 40.8444 | 52.2733 | 50.2321 | 47.946 | 44.3404 | 49.986 | 47.7396 | 49.9003 | 43.3645 | 44.524 | 42.3124 | 42.8436 | 35.5397 | 53.3557 | 61.0424 | 43.3006 | 49.968 | 63.7914 | 49.3939 | 52.8098 | 35.937 | 27.1912 | 94.0108 | 30.5107 | 28.6475 | 36.7066 | 31.7445 | 39.2769 | 33.9002 | 34.8058 | 35.4687 | 37.0559 | 38.5914 | 39.2743 | 40.3689 | 42.031
114 | 426A12 | 2023-11-20 19:05 | -27.8669 |  | 38.7425 | 54.4848 | 57.158 | 52.7702 | 50.64 | 52.7845 | 50.4421 | 46.2255 | 43.2243 | 48.6133 | 53.9556 | 49.9114 | 48.8659 | 62.5908 | 48.2159 | 49.849 | 61.0369 | 50.798 | 65.9543 | 46.925 | 34.8695 | 26.6445 | 94.049 | 32.1867 | 28.957 | 37.1329 | 30.9417 | 40.3822 | 33.4605 | 34.7246 | 35.6922 | 37.0816 | 37.6255 | 39.0263 | 40.2103 | 42.0719
115 | 426A12 | 2023-11-20 19:05 | -27.8766 |  | 57.9498 | 62.3388 | 59.7886 | 56.9537 | 54.2206 | 45.0598 | 47.1131 | 44.5509 | 41.6771 | 47.598 | 50.9552 | 50.3993 | 50.4903 | 63.8154 | 43.1448 | 53.2417 | 61.5501 | 47.264 | 55.3799 | 50.1266 | 46.0092 | 36.1902 | 93.7832 | 31.5691 | 28.8737 | 37.2159 | 30.5968 | 40.2709 | 33.713 | 34.5578 | 35.4887 | 36.4284 | 37.7615 | 38.6586 | 39.625 | 41.6126
116 | 426A12 | 2023-02-23 12:01 | -27.6151 |  | 77.9525 | 91.9352 | 117.9786 | 101.9913 | 88.7001 | 63.1901 | 58.9727 | 65.0877 | 57.4265 | 49.3684 | 51.7362 | 54.5343 | 53.6403 | 61.5604 | 48.8552 | 49.593 | 47.839 | 43.8295 | 39.4879 | 36.5621 | 31.4008 | 26.8111 | 94.0181 | 32.0879 | 29.4668 | 38.9077 | 31.3279 | 39.4565 | 33.5834 | 34.1927 | 35.4367 | 36.7386 | 37.9714 | 39.0069 | 39.899 | 41.6687
117 | 426A12 | 2023-02-23 10:53 | -27.5916 |  | 79.7351 | 65.2636 | 56.2039 | 53.749 | 54.8024 | 60.6884 | 60.2683 | 62.2322 | 54.7863 | 52.0811 | 55.5459 | 53.9997 | 53.658 | 58.1118 | 47.2426 | 46.1335 | 44.5565 | 39.9007 | 37.1651 | 33.7086 | 26.6138 | 26.0799 | 94.0662 | 31.1488 | 29.9178 | 39.0526 | 30.8668 | 39.3457 | 33.3801 | 34.4043 | 35.3299 | 36.5609 | 37.9215 | 38.8909 | 39.9579 | 41.8248
118 | 426A12 | 2023-02-23 10:53 | -27.6163 |  | 81.9158 | 89.5264 | 97.2222 | 87.6579 | 79.1309 | 59.7917 | 59.0052 | 57.1801 | 53.5462 | 52.2878 | 44.8622 | 50.0936 | 51.528 | 53.6252 | 46.518 | 47.4094 | 44.631 | 40.6592 | 37.4196 | 33.4982 | 27.9261 | 25.5348 | 92.444 | 30.4158 | 27.5701 | 37.3358 | 28.8826 | 38.1658 | 31.747 | 32.7518 | 33.927 | 35.1401 | 36.3877 | 37.5301 | 38.4345 | 39.9934

## AIIC POS 1
| 1/1 Octave | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28 | Unnamed: 29 | Unnamed: 30 | Unnamed: 31 | Unnamed: 32 | Unnamed: 33 | Unnamed: 34 | Unnamed: 35 | Unnamed: 36
0 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
1 | Overall 1/1 Spectra | 61.4 | 65.4 | 78.5 | 77.4 | 82.9 | 78.9 | 69.1 | 52 | 46.7 | 38.9 | 30 | 21.1
2 | Max 1/1 Spectra | 72.5 | 71.9 | 84.4 | 82.6 | 87.1 | 84.3 | 72.2 | 54.4 | 48.4 | 40.9 | 33.2 | 28.8
3 | Min 1/1 Spectra | 57.2 | 59.5 | 69.6 | 66.9 | 79.3 | 76.2 | 67.8 | 50.7 | 44.7 | 37.7 | 28.3 | 19
4
5 | 1/3 Octave
6 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
7 | Overall 1/3 Spectra | 56 | 51.9 | 59.4 | 57.4 | 61.9 | 61.6 | 65.8 | 76.4 | 73.8 | 67.4 | 72.6 | 74.9 | 78.6 | 79.7 | 74.9 | 72.9 | 76 | 72.5 | 68 | 60.8 | 55.8 | 49.7 | 45 | 44.5 | 42.4 | 43.2 | 38.8 | 36.5 | 33.5 | 30.7 | 27.5 | 24.9 | 21.2 | 17.3 | 16.3 | 14.6
8 | Max 1/3 Spectra | 68.1 | 63.9 | 64.8 | 61.1 | 70.1 | 65.6 | 72.6 | 83.3 | 78.8 | 72.8 | 79.9 | 79.3 | 82.8 | 84.4 | 78.6 | 76 | 80 | 76.4 | 69.6 | 63 | 58.1 | 52 | 47.1 | 46.4 | 44 | 45.2 | 40 | 38.1 | 36.5 | 33.2 | 31 | 28.2 | 24.6 | 22.8 | 23 | 28.5
9 | Min 1/3 Spectra | 36.8 | 41.3 | 49.5 | 51.6 | 55.4 | 53 | 54.6 | 60.6 | 64.3 | 51.1 | 62.9 | 69.6 | 71.6 | 69.2 | 63.5 | 69.3 | 72.3 | 69.8 | 66.3 | 59.3 | 49.3 | 47.7 | 39.2 | 43.1 | 40.8 | 38.6 | 36 | 34.5 | 31.1 | 28.5 | 25.7 | 23 | 18.8 | 15.5 | 13.2 | 12.3
10
11 | L(20-200Hz) | 85.3612
12
13
14 | 1/1 OBA Ref. Spectra
15 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20
21 | 1/3 OBA Ref. Spectra
22 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27
28
29 | 1/1 OBA Under Range
30 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
31 | Under Range Limit | 33.9 | 30.7 | 28.9 | 27.9 | 24.9 | 18.9 | 16.9 | 20.9 | 18.9 | 21 | 22.7 | 24.9
32 | Noise Floor | 16.1 | 14.8 | 10.8 | 8.3 | 6.9 | 5.8 | 6.7 | 8 | 9.7 | 11.9 | 13.5 | 14.8
33
34 | 1/3 OBA Under Range
35 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
36 | Under Range Limit | 37.9 | 34.9 | 30.9 | 33.5 | 32.7 | 30.7 | 27.9 | 23.9 | 23.9 | 22.9 | 21.9 | 25.9 | 24.9 | 21.9 | 20.9 | 21.9 | 15.9 | 12.9 | 13.9 | 19.9 | 12.9 | 14.9 | 13.9 | 12.8 | 13.3 | 14.2 | 14.9 | 15.7 | 16.3 | 16.9 | 17.5 | 17.9 | 18.9 | 19.9 | 19.9 | 21.7
37 | Noise Floor | 14.3 | 11.6 | 10.3 | 10.8 | 8.9 | 8 | 7.5 | 7.3 | 5.6 | 3.6 | 3.6 | 3.4 | 2.8 | 1.2 | 1.1 | 1.3 | 0.7 | 1.3 | 2 | 2.2 | 2.4 | 2.6 | 3 | 3.6 | 4.2 | 5.1 | 5.7 | 6.5 | 7.1 | 7.8 | 8.3 | 8.8 | 9.1 | 9.7 | 9.9 | 10.9

## AIIC POS 2
| 1/1 Octave | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28 | Unnamed: 29 | Unnamed: 30 | Unnamed: 31 | Unnamed: 32 | Unnamed: 33 | Unnamed: 34 | Unnamed: 35 | Unnamed: 36
0 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
1 | Overall 1/1 Spectra | 62 | 66.3 | 78.5 | 76.7 | 81.4 | 77.5 | 68.6 | 52.8 | 49.1 | 38.9 | 29.9 | 21.3
2 | Max 1/1 Spectra | 65.4 | 70.1 | 84.3 | 81.5 | 85.1 | 80.9 | 70.8 | 54.7 | 50.5 | 40.7 | 32.9 | 25.5
3 | Min 1/1 Spectra | 56.6 | 59.6 | 68.9 | 72.2 | 77.7 | 75 | 66.8 | 51.6 | 47.9 | 37.6 | 27.6 | 18.4
4
5 | 1/3 Octave
6 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
7 | Overall 1/3 Spectra | 51.9 | 51 | 61 | 61.7 | 61.8 | 61.6 | 68.2 | 76.9 | 72.2 | 66.8 | 72.1 | 74.3 | 77.1 | 78.4 | 72.1 | 72 | 74.3 | 71.5 | 67.1 | 62.5 | 54.8 | 49 | 45.8 | 48.4 | 45.5 | 45.2 | 40.8 | 37.1 | 32.5 | 30.1 | 27.4 | 24.5 | 21.4 | 17.3 | 16.6 | 15.1
8 | Max 1/3 Spectra | 59.2 | 56.6 | 64.5 | 65.7 | 66.7 | 66.2 | 75.4 | 83.6 | 77.1 | 73 | 79 | 79.3 | 81 | 82.9 | 76.1 | 74.6 | 78 | 74.9 | 69.2 | 64.7 | 56.6 | 51.2 | 48.5 | 50.4 | 47.1 | 46.7 | 42.2 | 39 | 34.5 | 32.4 | 30.4 | 27.9 | 24.4 | 20.1 | 21.4 | 20.5
9 | Min 1/3 Spectra | 39.6 | 42.5 | 54.6 | 53.7 | 53.7 | 55.8 | 60.4 | 64.6 | 60.9 | 53.3 | 62.3 | 69.4 | 72.2 | 72.9 | 66.1 | 68.5 | 72 | 68.4 | 64.8 | 61 | 53 | 47.7 | 44 | 47 | 44 | 44 | 39.8 | 35.6 | 31.3 | 27.8 | 25.3 | 21.9 | 18.5 | 13.7 | 13.4 | 12.5
10
11 | L(20-200Hz) | 84.3788
12
13
14 | 1/1 OBA Ref. Spectra
15 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20
21 | 1/3 OBA Ref. Spectra
22 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27
28
29 | 1/1 OBA Under Range
30 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
31 | Under Range Limit | 33.9 | 30.7 | 28.9 | 27.9 | 24.9 | 18.9 | 16.9 | 20.9 | 18.9 | 21 | 22.7 | 24.9
32 | Noise Floor | 16.1 | 14.8 | 10.8 | 8.3 | 6.9 | 5.8 | 6.7 | 8 | 9.7 | 11.9 | 13.5 | 14.8
33
34 | 1/3 OBA Under Range
35 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
36 | Under Range Limit | 37.9 | 34.9 | 30.9 | 33.5 | 32.7 | 30.7 | 27.9 | 23.9 | 23.9 | 22.9 | 21.9 | 25.9 | 24.9 | 21.9 | 20.9 | 21.9 | 15.9 | 12.9 | 13.9 | 19.9 | 12.9 | 14.9 | 13.9 | 12.8 | 13.3 | 14.2 | 14.9 | 15.7 | 16.3 | 16.9 | 17.5 | 17.9 | 18.9 | 19.9 | 19.9 | 21.7
37 | Noise Floor | 14.3 | 11.6 | 10.3 | 10.8 | 8.9 | 8 | 7.5 | 7.3 | 5.6 | 3.6 | 3.6 | 3.4 | 2.8 | 1.2 | 1.1 | 1.3 | 0.7 | 1.3 | 2 | 2.2 | 2.4 | 2.6 | 3 | 3.6 | 4.2 | 5.1 | 5.7 | 6.5 | 7.1 | 7.8 | 8.3 | 8.8 | 9.1 | 9.7 | 9.9 | 10.9

## AIIC POS 3
| 1/1 Octave | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28 | Unnamed: 29 | Unnamed: 30 | Unnamed: 31 | Unnamed: 32 | Unnamed: 33 | Unnamed: 34 | Unnamed: 35 | Unnamed: 36
0 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
1 | Overall 1/1 Spectra | 60.2 | 64.8 | 76 | 76.4 | 82.2 | 77.5 | 68.1 | 50.2 | 47.6 | 38.8 | 30 | 21.1
2 | Max 1/1 Spectra | 66.6 | 69 | 80.3 | 81.6 | 86.3 | 80.1 | 70.2 | 51.7 | 49.2 | 40.7 | 33.2 | 26.1
3 | Min 1/1 Spectra | 56 | 52.1 | 68.1 | 71.1 | 77.6 | 74.4 | 66.7 | 48.9 | 45.8 | 36.7 | 26.9 | 18.1
4
5 | 1/3 Octave
6 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
7 | Overall 1/3 Spectra | 51.8 | 51.4 | 58.4 | 56.9 | 60.6 | 61.4 | 66.7 | 72.8 | 72.2 | 67.3 | 70.8 | 74.1 | 77.9 | 79.6 | 72.1 | 72.5 | 74.1 | 71.2 | 66.9 | 61.2 | 53.5 | 46.6 | 43.6 | 45.4 | 42.9 | 44.3 | 39.9 | 36.9 | 33 | 29.8 | 27.4 | 25 | 21.7 | 17.8 | 16 | 14.3
8 | Max 1/3 Spectra | 58 | 60.5 | 62.8 | 61.3 | 65.6 | 65.3 | 73.4 | 78 | 76.4 | 72.7 | 77.5 | 79.3 | 81.9 | 84.8 | 76.7 | 76.4 | 77.4 | 74.9 | 68.8 | 63.5 | 55.7 | 48.2 | 44.9 | 47.1 | 44.5 | 46.3 | 41.6 | 38.9 | 34.8 | 32.1 | 30.2 | 28.9 | 24.9 | 22.1 | 21.7 | 22
9 | Min 1/3 Spectra | 45 | 42.3 | 53.7 | 47.6 | 42.8 | 50.4 | 55.9 | 60.9 | 62.4 | 56 | 59.8 | 67.4 | 66.2 | 73.6 | 66.8 | 68.6 | 68.8 | 68.3 | 65.1 | 58.9 | 51.3 | 42.5 | 41.9 | 44.1 | 41.4 | 42.1 | 37.5 | 34.5 | 29.9 | 27 | 23.9 | 21.5 | 17.9 | 14.6 | 12.7 | 12.3
10
11 | L(20-200Hz) | 84.3404
12
13
14 | 1/1 OBA Ref. Spectra
15 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20
21 | 1/3 OBA Ref. Spectra
22 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27
28
29 | 1/1 OBA Under Range
30 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
31 | Under Range Limit | 33.9 | 30.7 | 28.9 | 27.9 | 24.9 | 18.9 | 16.9 | 20.9 | 18.9 | 21 | 22.7 | 24.9
32 | Noise Floor | 16.1 | 14.8 | 10.8 | 8.3 | 6.9 | 5.8 | 6.7 | 8 | 9.7 | 11.9 | 13.5 | 14.8
33
34 | 1/3 OBA Under Range
35 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
36 | Under Range Limit | 37.9 | 34.9 | 30.9 | 33.5 | 32.7 | 30.7 | 27.9 | 23.9 | 23.9 | 22.9 | 21.9 | 25.9 | 24.9 | 21.9 | 20.9 | 21.9 | 15.9 | 12.9 | 13.9 | 19.9 | 12.9 | 14.9 | 13.9 | 12.8 | 13.3 | 14.2 | 14.9 | 15.7 | 16.3 | 16.9 | 17.5 | 17.9 | 18.9 | 19.9 | 19.9 | 21.7
37 | Noise Floor | 14.3 | 11.6 | 10.3 | 10.8 | 8.9 | 8 | 7.5 | 7.3 | 5.6 | 3.6 | 3.6 | 3.4 | 2.8 | 1.2 | 1.1 | 1.3 | 0.7 | 1.3 | 2 | 2.2 | 2.4 | 2.6 | 3 | 3.6 | 4.2 | 5.1 | 5.7 | 6.5 | 7.1 | 7.8 | 8.3 | 8.8 | 9.1 | 9.7 | 9.9 | 10.9

## AIIC POS 4
| 1/1 Octave | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28 | Unnamed: 29 | Unnamed: 30 | Unnamed: 31 | Unnamed: 32 | Unnamed: 33 | Unnamed: 34 | Unnamed: 35 | Unnamed: 36
0 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
1 | Overall 1/1 Spectra | 61.5 | 67.5 | 73.8 | 73.7 | 81.8 | 77.8 | 69.5 | 50.5 | 48.2 | 37.4 | 28.8 | 20.2
2 | Max 1/1 Spectra | 66.1 | 72.2 | 78.1 | 78.6 | 85.6 | 80.3 | 71.3 | 52.6 | 49.4 | 39 | 31.6 | 23.6
3 | Min 1/1 Spectra | 53 | 60.3 | 64.4 | 66 | 76.1 | 75.7 | 67.8 | 49 | 47.1 | 36 | 26.9 | 18.1
4
5 | 1/3 Octave
6 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
7 | Overall 1/3 Spectra | 51.5 | 50.6 | 60.4 | 55.2 | 65.3 | 62.7 | 63.7 | 71.6 | 68.6 | 67.7 | 69 | 69.5 | 73.3 | 79.2 | 76.8 | 75.1 | 72.1 | 71.1 | 68.4 | 62.2 | 52.7 | 47.9 | 43 | 44.7 | 44.5 | 44.8 | 39 | 35.4 | 31.6 | 28.8 | 26.1 | 23.6 | 20.5 | 16.6 | 15 | 14
8 | Max 1/3 Spectra | 57.3 | 56.6 | 65.5 | 61.5 | 70.1 | 67.5 | 69.5 | 76.9 | 72.9 | 72.6 | 74.6 | 74.2 | 78.3 | 83.7 | 80.4 | 78.4 | 75.9 | 74 | 70.5 | 63.9 | 55.2 | 50.4 | 44.8 | 46.6 | 46.1 | 46.1 | 40.3 | 36.8 | 33.6 | 30.9 | 28.9 | 26.9 | 23.5 | 19.5 | 18.7 | 17.9
9 | Min 1/3 Spectra | 45.1 | 41.9 | 46.7 | 45.1 | 58.3 | 53.2 | 52.3 | 56.4 | 57.7 | 52.9 | 59.8 | 62.6 | 64.1 | 73.5 | 70.3 | 71.5 | 70.1 | 68.7 | 66.5 | 60 | 50.9 | 46.1 | 41.6 | 43.4 | 43.3 | 43.5 | 37.9 | 33.9 | 29.8 | 27.3 | 24.3 | 21.3 | 17.8 | 14.1 | 12.4 | 12.4
10
11 | L(20-200Hz) | 83.6815
12
13
14 | 1/1 OBA Ref. Spectra
15 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20
21 | 1/3 OBA Ref. Spectra
22 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27
28
29 | 1/1 OBA Under Range
30 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
31 | Under Range Limit | 33.9 | 30.7 | 28.9 | 27.9 | 24.9 | 18.9 | 16.9 | 20.9 | 18.9 | 21 | 22.7 | 24.9
32 | Noise Floor | 16.1 | 14.8 | 10.8 | 8.3 | 6.9 | 5.8 | 6.7 | 8 | 9.7 | 11.9 | 13.5 | 14.8
33
34 | 1/3 OBA Under Range
35 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
36 | Under Range Limit | 37.9 | 34.9 | 30.9 | 33.5 | 32.7 | 30.7 | 27.9 | 23.9 | 23.9 | 22.9 | 21.9 | 25.9 | 24.9 | 21.9 | 20.9 | 21.9 | 15.9 | 12.9 | 13.9 | 19.9 | 12.9 | 14.9 | 13.9 | 12.8 | 13.3 | 14.2 | 14.9 | 15.7 | 16.3 | 16.9 | 17.5 | 17.9 | 18.9 | 19.9 | 19.9 | 21.7
37 | Noise Floor | 14.3 | 11.6 | 10.3 | 10.8 | 8.9 | 8 | 7.5 | 7.3 | 5.6 | 3.6 | 3.6 | 3.4 | 2.8 | 1.2 | 1.1 | 1.3 | 0.7 | 1.3 | 2 | 2.2 | 2.4 | 2.6 | 3 | 3.6 | 4.2 | 5.1 | 5.7 | 6.5 | 7.1 | 7.8 | 8.3 | 8.8 | 9.1 | 9.7 | 9.9 | 10.9

## AIIC Source
| 1/1 Octave | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28 | Unnamed: 29 | Unnamed: 30 | Unnamed: 31 | Unnamed: 32 | Unnamed: 33 | Unnamed: 34 | Unnamed: 35 | Unnamed: 36
0 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
1 | Overall 1/1 Spectra | 70.7 | 73.3 | 82.4 | 71.3 | 84.7 | 84.5 | 82 | 78.3 | 73.5 | 70.3 | 74.4 | 66.2
2 | Max 1/1 Spectra | 80.4 | 79.2 | 83.9 | 75.7 | 86.6 | 85.8 | 83.9 | 81.1 | 76.6 | 73 | 77.4 | 69.3
3 | Min 1/1 Spectra | 60.5 | 60 | 53.2 | 53.8 | 78.1 | 78.4 | 76.5 | 75.3 | 70 | 66.9 | 70.4 | 62.2
4
5 | 1/3 Octave
6 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
7 | Overall 1/3 Spectra | 69.2 | 61.9 | 62.1 | 60.7 | 71.7 | 67.4 | 70.7 | 81.8 | 70.8 | 67 | 66.2 | 66.4 | 73.5 | 81.9 | 80.8 | 78.1 | 80.3 | 80.4 | 79.5 | 76.3 | 74.8 | 73.7 | 73.1 | 73.9 | 70.7 | 67.8 | 66 | 66.8 | 65.2 | 64.3 | 67.5 | 71.5 | 69.1 | 64.3 | 60.3 | 53.7
8 | Max 1/3 Spectra | 79.4 | 72.5 | 67.3 | 67.6 | 78.9 | 69.4 | 73.5 | 83.6 | 74.8 | 69.6 | 69.2 | 73.1 | 79.3 | 84.1 | 83.4 | 80.6 | 82.3 | 83.1 | 81.5 | 79.1 | 77.8 | 77.2 | 77.1 | 76.5 | 73.9 | 71.1 | 68.7 | 69.3 | 68.2 | 67.4 | 70.6 | 74.7 | 71.9 | 67.5 | 64.8 | 58.4
9 | Min 1/3 Spectra | 54.3 | 50.7 | 53.1 | 50.8 | 58.4 | 53.4 | 51.4 | 43.8 | 45.2 | 37 | 36.5 | 33.9 | 62 | 74.5 | 70.8 | 72 | 72.8 | 74.3 | 73.8 | 72.5 | 69.3 | 70.5 | 69.8 | 70.5 | 67.6 | 64.4 | 62.9 | 63.3 | 61.9 | 61 | 63.1 | 67.3 | 64.7 | 60.7 | 55.2 | 48.1
10
11 | L(20-200Hz) | 87.4526
12
13 | LZS1.00 | 78.9 | 71.6 | 66.8 | 66.4 | 78.4 | 69 | 73.1 | 83.3 | 74.5 | 69.5 | 69 | 72.7 | 79.1 | 84 | 83.1 | 80.3 | 82 | 82.6 | 81.2 | 78.8 | 77.5 | 77 | 76.7 | 76.1 | 73.4 | 70.6 | 68.3 | 69.1 | 68 | 67.1 | 70.3 | 74.4 | 71.7 | 67.3 | 64.4 | 58.1
14 | LZS10.00 | 73.2 | 64.9 | 64.4 | 63.5 | 73.6 | 68.4 | 72.3 | 82.7 | 73.9 | 68.6 | 67.8 | 69.9 | 76.7 | 83.5 | 82.7 | 79.5 | 81.2 | 81.6 | 80.5 | 77.7 | 76.1 | 75.3 | 74.5 | 75 | 71.8 | 68.9 | 67.1 | 68.1 | 66.3 | 65.5 | 68.4 | 72.7 | 70.1 | 66 | 62.1 | 55.7
15 | LZS33.30 | 68.1 | 61.3 | 62.7 | 61.1 | 72.2 | 67.8 | 71.2 | 82.3 | 71.2 | 67.6 | 66.5 | 65.2 | 73.5 | 82.8 | 81.7 | 78.6 | 80.6 | 80.6 | 79.9 | 76.5 | 75 | 73.9 | 73.3 | 74.3 | 71 | 68.2 | 66.1 | 67.1 | 65.5 | 64.5 | 67.5 | 71.5 | 69.2 | 64.6 | 60.4 | 53.8
16 | LZS50.00 | 65.6 | 59 | 61.5 | 59.7 | 70.9 | 67.5 | 70.6 | 82.1 | 69.2 | 67.1 | 66 | 64.1 | 72 | 81.6 | 80.5 | 78.1 | 80.2 | 80.3 | 79.4 | 76.1 | 74.7 | 73.4 | 72.8 | 74 | 70.6 | 67.6 | 65.9 | 66.7 | 65 | 64.1 | 67.3 | 71.2 | 68.9 | 63.9 | 59.6 | 52.8
17 | LZS66.60 | 63.8 | 56.8 | 60.3 | 58.5 | 70.1 | 67.2 | 70.1 | 81.7 | 68.1 | 66.6 | 65.3 | 63.2 | 70.1 | 80.5 | 79.4 | 77.2 | 79.8 | 79.9 | 78.9 | 75.7 | 74.4 | 72.9 | 72.3 | 73.7 | 70.3 | 67.2 | 65.7 | 66.5 | 64.9 | 63.9 | 67.1 | 71 | 68.7 | 63.6 | 59.2 | 52.3
18 | LZS90.00 | 57.4 | 54.1 | 58.5 | 54.6 | 67.1 | 65.9 | 67.4 | 79.8 | 67 | 63.6 | 64 | 61.3 | 68.6 | 79.6 | 77.5 | 76.1 | 78.8 | 79 | 78.1 | 74.9 | 73.6 | 71.7 | 71.2 | 71.6 | 69 | 66.4 | 64.1 | 64.6 | 63.3 | 62.7 | 66.1 | 70.4 | 67.7 | 63.2 | 58.7 | 51.7
19
20
21 | 1/1 OBA Ref. Spectra
22 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27
28 | 1/3 OBA Ref. Spectra
29 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34
35
36 | 1/1 OBA Under Range
37 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
38 | Under Range Limit | 62.7 | 55.8 | 53.8 | 48.8 | 45.8 | 46.8 | 50.8 | 45.9 | 48.9 | 50.8 | 52.8 | 55.8
39 | Noise Floor | 32.7 | 32.7 | 31.2 | 30.3 | 31.9 | 31.9 | 34.3 | 32.6 | 34.5 | 37.6 | 41.1 | 44.4
40
41 | 1/3 OBA Under Range
42 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
43 | Under Range Limit | 52.8 | 49.8 | 48.8 | 49.8 | 49.8 | 48.8 | 46.8 | 47.8 | 47.8 | 45.8 | 43.8 | 42.8 | 43.8 | 44.8 | 40.8 | 41.8 | 41.8 | 39.8 | 43.8 | 42.8 | 39.9 | 40.9 | 43.8 | 41.8 | 40.8 | 40.8 | 41.8 | 44.8 | 43.9 | 45.9 | 47.8 | 49.8 | 48.9 | 49.9 | 50.8 | 52.8
44 | Noise Floor | 28.4 | 27.5 | 29.2 | 29 | 26.3 | 28.5 | 26.5 | 27.3 | 26.5 | 26 | 26.5 | 26.6 | 25.8 | 25.4 | 26 | 26.4 | 28.5 | 27.3 | 26.8 | 26.7 | 26.7 | 27.4 | 27.8 | 28.7 | 29.2 | 29.7 | 30.7 | 31.8 | 32.8 | 34 | 34.7 | 36.3 | 37.4 | 38.4 | 39.4 | 41

## AIIC CARPET
| 1/1 Octave | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | Unnamed: 25 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28 | Unnamed: 29 | Unnamed: 30 | Unnamed: 31 | Unnamed: 32 | Unnamed: 33 | Unnamed: 34 | Unnamed: 35 | Unnamed: 36
0 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
1 | Overall 1/1 Spectra | 62.8 | 63.6 | 77.8 | 76.8 | 77.8 | 67.1 | 50 | 39.9 | 38.6 | 32.3 | 25.3 | 18.6
2 | Max 1/1 Spectra | 72.9 | 67.5 | 82.8 | 83.3 | 81.7 | 70 | 55.6 | 49 | 51 | 46.1 | 41.9 | 33.8
3 | Min 1/1 Spectra | 51.6 | 56.6 | 68.2 | 72 | 74.6 | 64.5 | 48.3 | 38.1 | 37.2 | 30.9 | 23.6 | 17.2
4
5 | 1/3 Octave
6 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
7 | Overall 1/3 Spectra | 57.9 | 55 | 62 | 53.1 | 59.1 | 61.1 | 63.9 | 76 | 72.3 | 66.4 | 73.4 | 73.5 | 75.1 | 73.8 | 67.8 | 64.4 | 62.7 | 56.4 | 48.5 | 42.8 | 37.6 | 35.7 | 33.8 | 35.9 | 33.8 | 35.2 | 31.6 | 29.8 | 26.9 | 24.6 | 22.3 | 20.4 | 17.7 | 15 | 13.4 | 12.5
8 | Max 1/3 Spectra | 72 | 67.5 | 66.7 | 64 | 63.4 | 65.3 | 70.6 | 82 | 77 | 71.8 | 81.7 | 78.5 | 80.4 | 78.6 | 71 | 67.2 | 66 | 60 | 53 | 50 | 48.8 | 43.6 | 43.8 | 45.9 | 46.6 | 45 | 43.2 | 43 | 39.7 | 38.7 | 40.8 | 34.6 | 34.5 | 29.8 | 27.4 | 28.7
9 | Min 1/3 Spectra | 41.7 | 42.9 | 48 | 46 | 50.1 | 51.9 | 51.7 | 64.4 | 60.6 | 52.5 | 62.9 | 69.9 | 70.2 | 66.9 | 61 | 61.3 | 59.8 | 53.7 | 46.2 | 41.2 | 35.7 | 33.1 | 30.6 | 34.2 | 32.4 | 33.6 | 30 | 28.9 | 24.9 | 22.6 | 20.8 | 18.4 | 15.9 | 13.3 | 11.8 | 11.7
10
11 | L(20-200Hz) | 82.4128
12
13
14 | 1/1 OBA Ref. Spectra
15 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20
21 | 1/3 OBA Ref. Spectra
22 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27
28
29 | 1/1 OBA Under Range
30 | Frequency (Hz) | 8 | 16 | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | 16000
31 | Under Range Limit | 33.9 | 30.7 | 28.9 | 27.9 | 24.9 | 18.9 | 16.9 | 20.9 | 18.9 | 21 | 22.7 | 24.9
32 | Noise Floor | 16.1 | 14.8 | 10.8 | 8.3 | 6.9 | 5.8 | 6.7 | 8 | 9.7 | 11.9 | 13.5 | 14.8
33
34 | 1/3 OBA Under Range
35 | Frequency (Hz) | 6.3 | 8 | 10 | 12.5 | 16 | 20 | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | 12500 | 16000 | 20000
36 | Under Range Limit | 37.9 | 34.9 | 30.9 | 33.5 | 32.7 | 30.7 | 27.9 | 23.9 | 23.9 | 22.9 | 21.9 | 25.9 | 24.9 | 21.9 | 20.9 | 21.9 | 15.9 | 12.9 | 13.9 | 19.9 | 12.9 | 14.9 | 13.9 | 12.8 | 13.3 | 14.2 | 14.9 | 15.7 | 16.3 | 16.9 | 17.5 | 17.9 | 18.9 | 19.9 | 19.9 | 21.7
37 | Noise Floor | 14.3 | 11.6 | 10.3 | 10.8 | 8.9 | 8 | 7.5 | 7.3 | 5.6 | 3.6 | 3.6 | 3.4 | 2.8 | 1.2 | 1.1 | 1.3 | 0.7 | 1.3 | 2 | 2.2 | 2.4 | 2.6 | 3 | 3.6 | 4.2 | 5.1 | 5.7 | 6.5 | 7.1 | 7.8 | 8.3 | 8.8 | 9.1 | 9.7 | 9.9 | 10.9

## room_properties
| Source Room Name | Recieve Room Name | Testdate | ReportDate | Test number | Source Vol | Recieve Vol | Partition area | Partition dim. | Source room Finish | Recieve room Finish | Srs Floor Descrip. | Srs Ceiling Descrip. | Srs Walls Descrip. | Rec Floor Descrip. | Rec Ceiling Descrip. | Rec Walls Descrip. | Tested Assembly | Expected Performance | Annex 2 used? | Test assem. type | NIC reporting Note
0 | 2nd Floor Kitchen | 1st Floor Great Room/Kitchen | 2024-04-04 | 2024-04-18 | 1.2.1 | 3949 | 3949 | 428 | 14.8x29.583 | finished unfurnished | finished unfurnished | LVT | gyp | gyp | LVT | gyp | gyp | Floor-ceiling | Yes | No | Floor-ceiling | ---